## FOOD LION REMODEL – SUN REMODEL BID WALK THROUGH NOTES

## STORE # 2839 BEAUFORT, SC

DATE OF SCHEDULE PROVIDED AT BID:  7/27/22

STORE HOURS = 7am – 11pm

_________________________________________________________________________________

Important note:

ALL attached bid notes are specific and will override the drawings. General Contractor is responsible for the timely distribution of updated information to ALL sub’s and field personnel.

_________________________________________________________________________________

Standard Notes:

- The bid date for this project is August 10, 2022 at 2:00 pm.  This project will be bid through Retail Business Service's Project Management Site, PMWeb  https://rbs.pmweb.com.  For questions or support contact: Shana Hines at 704-310-4218 or shana.hines@retailbusinessservices.com

- Landlord Information: (Leased)

ACI Midtown Shopping Center

4081/2 State Street

Greensboro, NC 27405

Attn.: James Black

Ph. #336-383-5901

- All bids must contain name of plumbing, electrical, and HVAC contractor and their bid price.  Please 
submit all qualified sub prices and include a minimum of at least three per trade.  A copy of the bid 
cover page, showing the bid amount, is required.

- Food Lion will provide Builders Risk and Owners Protective Liability Insurance.  The contractor must provide liability insurance.

- PLEASE NOTE!  Contractor MUST include a payment and performance bond in the bid price IF THE JOB IS PRICED OVER $500,000.  The bonding company’s A M Best Rating must be B+6 to A-6.  Proof of this rating must accompany bond.  Bond rating MUST be within the past 30 days.

- GENERAL CONTRACTOR TO INCLUDE PERMIT FEES IN BID.

- North Carolina Only – General Contractor to include the Application Fee of $50 (or current applicable fee) to cover the cost of the Appointment of NC Lien Agent.

- Retail Business Services reserves the right to accept any bid or bid alternate, to reject any or all bids, or to waive any informalities in bids received where such acceptance, rejections, or waiver is considered to be in the best interest of Retail Business Services.

- IMPORTANT NOTE:  The awarded General Contractor must submit a “Schedule of Values” for this project when he submits his contract to the Retail Business Services Construction Project Coordinator.

- General Contractor shall provide unit pricing in bid proposal for the following items:

  - Rock excavation (Cubic yard).

  - Finished concrete (cubic yard).

  - Bad soil removal and replacement (cubic yards).

  - Asphalt removal and replacement (square yard).

- Food Lion’s standard new store specifications will govern all workmanship and materials. The General Contractor will be required to provide the bidding sub-contractors a copy of the store specifications which will be adhered to during construction. Any questions or discrepancies must be confirmed through the Construction Manager.

- IMPORTANT NOTE:  The General Contractor must incorporate the new Workflow billing procedures as set up by Retail Business Services Construction. Please contact Lori Bowen (704-310-3036) for any questions or concerns related to billing.

- IMPORTANT NOTE:  The awarded General Contractor is required to submit a partial Release of Lien, equal to the amount of the pay request, to accompany each Contractor’s Application for Payment.  Payment will not be made until each pay request has this information attached.

- General Contractor shall submit each change order within 45 days of the change order work completing.  Estimated change order cost should be communicated to the Construction Manager at the time the change order is communicated.

- General Contractor shall submit to Owner an application for Final Payment; all Change Orders are to be submitted and processed before submittal of the application for Final Payment. In the event General Contractor shall fail to make and present such application within one hundred eighty (180) days of Grand opening of a remodel or takeover, then any and all applications for such Final Payment shall be, and the same hereby are, waived and forever barred from collection by General Contractor from Owner.

- General Contractor shall video tape or photograph existing exterior conditions at store prior to any work beginning.  This should especially include the conditions of the roof, asphalt drives, landscaped and grass areas, and parking areas.  Any backcharges by the landlord that cannot be proven false by existing photographs will be paid by the General Contractor.

- General Contractor to provide on-site Superintendents with a digital camera for photos of all night work performed regarding trench lines, hub drains, etc.

- General Contractor to verify with local authorities and obtain/purchase any noise ordinance permits required.

- Drawings for Retail Business Services projects are housed on the company’s Project Management Site, PM Web. Each General Contractor is responsible for downloading their drawings (along with Refrigeration Summary, Asbestos Survey, Roof Survey and Food Lion Specifications) via the website. https://rbs.pmweb.com . There is no fee to download drawings from the site. For questions or support contact: Shana Hines at 704-310-4218 or shana.hines@retailbusinessservices.com

- General Contractor is responsible for verifying, obtaining, and incorporating the most current fixture plan and/or drawing revisions and distributing to the subs. Failure to obtain the most current fixture plan will result in the General Contractor having to make the necessary changes at their cost.

- General Contractor must ensure that all subs related to the remodel receive a copy of the refrigeration summary, asbestos survey, Food Lion Specification Book, etc. so the sub can research and incorporate a price appropriately for the work to include labor and material.

- General Contractor is responsible for providing a Superintendent for all subcontracted work under their contract.  A qualified Assistant Superintendent should be used for supervision above reasonable working hours of the Superintendent.  General Contractor is to be on site for the Construction Manager's weekly management site visit, and for all daytime inspections.

- General Contractor shall not remove the project Superintendent at any time unless approved by the appropriate RBS Construction Manager through completion of the project.

- General Contractor will be totally responsible for all construction and equipment related material that comes to the job site. Individuals who sign for equipment must review the material for any damages and must also ensure that everything is accounted for in the shipment. If this is not done with accurate detail; the General Contractor will be billed for equipment replacements. If there are concerns with the shipment, then contact the appropriate Construction Manager.  Refrigeration Contractor to be responsible for refrigerated items.

- General Contractor’s Project Manager is required to meet with the Construction Manager on a bi-weekly basis on the job site.

- A weekly meeting is required between the General Contractor and Store Manager to discuss the next (2) weeks work.  During scheduled night work, a meeting is required between the Safety PIC person and the GC to discuss safety items during that night's work.

- General Contractor must have all punch list items complete within three weeks of receiving it. If not, Retail Business Services Construction reserves the right to hire someone to complete the work at the General Contractors cost.

- SESCO will perform a punch-list on the Energy Management System and Test & Balance for the store at the time noted as “substantially complete” in the schedule. SESCO has one week to forward the punch-list and the General Contractor has two weeks to complete the punch-list. It will be the General Contractors responsibility to contact SESCO for the return visit upon completion of the punch-list. Any trips required for follow-up beyond this point will result in a back charge to the General Contractor.

- Retail Business Services Construction reserves the right to back charge subcontractors which do not show up for scheduled night work.  This may include labor cost for scheduled store personnel, store operating cost, etc.

- General Contractor to provide the store with a 24 hr. Emergency Contact List of all subs at the pre-construction meeting. General Contractor/Sub-Contractors to assume maintenance responsibility for the store at this point.  Emergency calls will be handled as such.  Any additional charges outside of the scope of work will be billed as a Maintenance Ticket.  A Maintenance Ticket must be entered to get paid.

- Smoking, eating, and drinking will only be allowed in an area designated by the Retail Business Services Construction Manager and the Store Manager.  General Contractor is to provide contracting subs a butt bucket for the rear exterior. All contractors are required to maintain their in-store purchase receipts and taped to the product while in the store.

- Shopping carts/floats are not to be used for construction purpose unless authorized by the Construction Manager.  Construction Carts may be provided, coordinate with Construction Manager.

- General Contractor to provide a storage container for equipment/materials/tools.  General Contractor must require their Electrical, Plumbing, and HVAC Contractors to provide storage containers.  Storage containers for all materials are a requirement throughout the remodel.  Only exception to this would be temperature acclamation for material (i.e.…VCT, Marlite, Acrovyn).  DO NOT store any tools, supplies, or building materials of any portion in the store.  Walk-in boxes and Mechanical Rooms are not allowed to be used for storage area. The General Contractor must coordinate with the Construction Manager and Store Manager for a designated interior storage area for deliveries and temporary storage (red tape zone).

- Maintenance Manager/Energy must require the Refrigeration Contractor to have a storage container on site to store refrigerated related materials and tools.  Energy Specialist/Refrigeration Contractor to contact the Construction Manager to locate the storage container prior to delivery.

- General Contractor will be responsible for “ALL” dumpster dumps including those for the Refrigeration Contractor and Grocery Reset.  General Contractor is responsible for the disposal of all removed gondola shelving and components once the Grocery Set Team has it palletized and moved to the dock. General Contractor will be responsible for all other discarded material during Grocery Reset.  Grocery reset may be completed prior to start of construction.  If this occurs, Retail Business Services provides dumpsters.

- General Contractor must use professional signage and neatly installed orange fencing for any detours required during the course of the remodel. Coordinate the use of dust walls vs. dust screens with Construction Manager.  Use 2x4 framed plywood dust walls with Tyvek (lettering turned inward and upside down) when any jack hammering, sawing, demolitions, etc. is taking place.  Dust walls need to be structural, lockable, and insulated where appropriate.  Dust screens should be constructed of 6mil. poly or painter’s cloth attached to the ceiling and secured at the floor by rolling a 2x4 in the excess material.  Dust screens are to be used for light construction to control dust and visibility only.  Food Lion grocery carts or wet floor signs are not allowed to be used as fencing supports.

- Retail Business Services will be supplying the Automatic Doors, Control Panels, Interior Lighting, Impact Doors, Sinks, Water Fountains, Water Heaters, Aqua stat & Stands, Hand Dryers and HVAC equipment.  Installation and warranties of this equipment is to be supplied by the General Contractor.  The General Contractor is responsible for ensuring that the SUB-CONTRACTORS order these items directly from the supplier as soon as the contract is awarded.  These items must be stored on site in the Sub-Contractors storage trailers.  A complete package with all the information will be sent to the awarded General Contractor.  National Account items MUST BE EXCLUDED from your bid, with the exception of installation and warranty.  General Contractor’s Project Manager must confirm that ALL orders have been made with delivery dates and provide documentation at the Pre-Construction Meeting.  First Pay Draw will not be released until all material orders have been verified. 

Please ENSURE you are copying the Equipment Coordinator noted on the order you place to the vendor as noted below for BETTER tracking.

Automatic Doors – Assa-Abloy / Besam – Jessica Shane @ 1-609-249-9498
Email:  Jessica.Shane@assaabloy.com; David.Hastings@retailbusinessservices.com

Power Wall-Electrical Switchgear – CD Controls – Contact: Ed Rios @ 706-476-7303 (Cell), Email:  edrios@cdcontrols.com

HVAC System/Energy Management/ Environmental Control – SESCO/McNamara – Contact: Erin Mariano @ 336-996-2220, Email erin.mariano@trs-SESCO.com or Penny Shepherd @ 336-996-2220, Email: penny@trs-SESCO.com

Interior Lighting Package – Wesco Lighting – Contact: Lisa Mastin @ 1-800-579-1514

Email:  lmastin@wesco.com

Site Lighting Package – Lighting Service Design/LSD – Contact:  Rick Donald @ 804-357-7840; Email:  rickdonald@lightingsolutions-design.com

Hollow Metal Doors & Hardware – B.A. Hoft – Contact: Joseph Holland @ 919-596-4446
Email:  jholland@bahoft.com

Dock Doors, Seals & Dock Leveler – Overhead Door – Contact: Amanda Cumberland 
@ 469-549-7025, Email:   Amanda_Cumberland@OverheadDoor.com; David.Hastings@retailbusinessservices.com

Traffic Doors – Hefco – Contact: Lisa Windle  @ 800-327-1817

Email:  cs4@hefcollc.com; David.Hastings@retailbusinessservices.com

Vestibule Carpet – Portico – Contact:  Bill Long @ 877-285-8899 x305

Email:  blong@porticosystems.com

Hand Dryers – George Scott & Associates – Contact: Bill Scott @ 704-376-4775

Email:  bill.scott@gsaclt.com

Sinks – John Boos – Contact: Lisa Windle @ 800-327-1817

Email:  cs4@hefcollc.com

Water Fountains, Water Heaters, Stands, and Aquastat (Therma-Stor) – WW Grainger  
Contact:  David.Hastings@retailbusinessservices.com; natalie.lebron@grainer.com

NOTE:  General Contractor to provide a list in each bid of the National Account items Retail Business Services is to supply.

- Plumbing Contractor is to order all new equipment through the National Account program, ALL other required repair parts can be purchased by the plumber outside of the National Accounts program once verified through the Construction Manager.

- Plumbing Contractor is to install/relocate hub drains as indicated on plans and bid notes.  4” bell hubs are required when two cases share one condensate hub in the floor.  4” bell hubs are required for new and relocated cases.  All exposed hubs shall be 4” bell type with PVC screen inserts; no more than ½” exposure above finished floor, unless otherwise required as per AHJ.  (No more than two cases can be piped to one hub, drains to hub can not run parallel.)  Plumbing Contractor will be required to install hubs as noted on the plans and shall not combine hubs in areas of new work.  The Plumbing Contractor MUST verify all hub drain placements with the drawings, case manufacturer specs, and the Construction Manager, if this is not done, all associated cost will be the Plumbing Contractors to pay.

- Refrigeration Contractor is to connect case drains to the hub drain. Case drains need to be cut on a 45° angle with an approved air gap as dictated by the local jurisdiction.  Case drains shall not be visible outside of the kick plates.

- Plumbing Contractor must run individual condensate drain lines off new/relocated evaporators. NO evaporate drain lines can be tee’d together.  ALL evaporator condensate lines are to be anchored to the wall with standoff brackets and hanger supports from the ceiling. Install plumbing escutcheons on wall penetrations.

- Plumbing Contractor must make all joints with compatible PVC or “No Hub” fittings, no “FERNCO” joints or "Gator Bite" type fittings will be accepted.

- TRENCH WORK:   All dirt shall be removed from the store and should never touch the floor.  Trenches	 shall be backfilled with aggregate no larger than #57, dowels must be installed in concrete on all pour backs and proper vapor barrier used.  Open trenches are to be covered with ¼” min. metal plate and matching carpet mats – trenches covered with plates/carpet are to be accompanied by orange safety cones and are allowed for a maximum of one week as temporary for inspections, once inspections have passed the General Contractor is to properly fill with concrete and install temporary VCT.  All pits should be photographed with current date to show interior before and after vapor barrier install and trench completion.  Photos are to be emailed to the appropriate Construction Manager.

- Fiberglass pits can be modified as needed to work around existing conduit, etc.  Exposed pits to have a min. 2" concrete cap flush with finished floor, pits under cases can be left without a cap but must be completely sealed.  All revised pits must be sealed completely to rodent proof and eliminate construction material from damaging the refrigeration lines. Special precautions need to be made when cutting holes in fiberglass boxes that they limit the amount of fiberglass that is cut away for line installations.  All new pits shall be fiberglass unless a fiberglass pit will not work, formed and poured concrete pits will be acceptable in this case. All pits should be photographed with current date to show interior before and after vapor barrier install and trench completion. Photos are to be emailed to the appropriate Construction Manager.

- Carpet mats are to be clean, same in color, and have rubber edges.  All mats are to be taped in place at all times. Mats are to be supplied by the General Contractor, do not use store's carpets.

- General Contractor to fill any abandoned pit with #57 stone and dowel in 4” concrete on vapor barrier.  Seal other end of PVC sleeve with rodent proof material as indicated in Specifications.

- It is mandatory on Food Lion projects when replacing the entire sales area ceilings, that the General Contractor recycles the ceiling tiles.  A separate storage trailer is required for each - new and recycled material.  Recyclable material must be kept dry.

- Any ceiling cleaning must be done by a professional cleaning company.  Ceiling cleaning contractors shall use cleaning mixtures that expose the ceiling tile to no more than 10 grams of water solution per square foot of ceiling tile, shall ensure that cleaning process does not create sagging or damage to the ceiling tile, and shall ensure that the operation will not adversely affect the performance or dimensional stability of the ceiling tile.  It will be the ceiling cleaning contractor’s responsibility to cover and protect the store product during the cleaning process.  The ceiling cleaning contractor shall not use any cleaning solutions that would have a corrosive effect on the ceiling grid or other metal surfaces in the store, which would eventually lead to the rusting or oxidizing of the metal surfaces.  The Ceiling Cleaning Contractor shall send a Material Safety Data Sheet (MSDS) for each store to Retail Business Services for our files as well as leaving a MSDS at each store while work is being done.

Approved ceiling contractors:

Keep Looking Up Acoustical Ceiling Cleaning & Services

Contact: Michael Tuczynski

Ph: Michael - 910-793-8200 or 910-443-6864

E-mail: cleaningk@bellsouth.net or mjt_klu@bellsouth.net

Team ATG

Contact:  Angie Kirsch

Ph: 800-334-1789 or 740-317-4204

Email:  angie@teamatg.com

Southern Cleaning

Contact:  Dennis Wilczewski

Ph: 864-325-1094

Email:  southerncleaning@rocketmail.com

Carolina Ceiling Cleaning, Inc.

Contact:  Mike Allred

Ph:  336-953-5433

Email:  mike@carolinaceilingclean.com

- Energy/Refrigeration Contractor must take appropriate actions as listed below and coordinate with Nick Cordasci at Retail Business Services 704-633-8250 ext. 4824 to report these issues.

- If refrigerant is recovered from any of our equipment, we must document and track the amount of refrigerant and its present location.

- If refrigerant is added to any of our equipment, we must document the amount of refrigerant, the date and the reason for the added refrigerant.

- If refrigerant is leaked accidentally (due to human error), we must document it.

- Electrical Contractor to provide a Commercial Qualified Lead Electrician for each project.  This person is to be identified as the Project Electrician and is to work on site a minimum of 40 hours each week starting from week 1 of the Construction Schedule to 100% complete.  Exceptions to this are Reset week and Holidays if no work is scheduled, special circumstances can be approved by Construction Manager only.

- Electrical Contractor shall install all vertical low voltage cabling in finished and unfinished areas in EMT with a 90° bend at the bar joist in the direction of the cable run.

- Electrical Contractor shall install and adequately secure ALL covers.  Provide or replace covers and fasteners and plug any holes as required.  Device covers in Meat, Produce, Deli/Bakery, and Exterior shall be weatherproof (WP) and in proper condition at closeout.  Vacuum branch circuit panel board, SweatMiser, and LiteMiser interiors and clean the tops of all electrical panels, cabinets, and troughs.

- Electrical Contractor shall install all low voltage cabling running overhead in the bar joist and tied every 15 ft.  Cabling that is suspended from the bar joist or lying on a ceiling will not be accepted.  Electrical Contractor is to work with each Food Lion vendor to remove any and all abandoned low voltage cabling.

- Electrical Contractor is to run all required low voltage sensor wires for cases as part of a preliminary scope of work at the beginning of the project. This scope includes connections into a junction trough in motor room; including conduit runs to racks.  No “free hanging” sensor wires allowed.

- Electrical Contractor is to properly label all main panels, service disconnects, sub-panels, breakers, branch circuit panel boards and disconnects that are not currently or correctly labeled.  Must use attachable name plate, phenolic as described in the specifications.

- Electrical Contractor must provide labor and material to go through ALL existing electrical panels to trace and verify all circuits for accuracy and install new updated panel schedules inside the panel board cabinets, both new and existing.  All schedules are to be on card stock, typed, and dated and installed in a clear pocket.  Electronic copies of all panel schedules are required at closeout.  (Do not remove existing panel schedules).

LABELING:  Receptacles and lighting are to be labeled by area/location.  Sales floor lighting circuits are to include row number.  Case circuits are to reference refrigeration circuits.  Spare is a breaker with no wire, Blank is an empty slot.  All wired and active breakers shall be properly scheduled.  Wired breakers with no active load – device shall be labeled as Spare, Ending Location.

- An RBS Vendor Team will install the front-end equipment; this includes and is limited to the following:  all check stands, cigarette kiosk, and Customer Service counters.  This includes setting and handling all equipment, clean and dirty power, associated CAT5 and Beldon cables.  This work will be permitted separate from other work in this project by the RBS Vendor Team.

- Electrical Contractor is not allowed to use Armored Cable (BX or MC) for electrical runs.  EMT must be used to connect panel to junction box.  Armored Cable is only allowed as fixture whips or extensions from a junction box above sales area ceiling to self-contained cases/equipment below (remote cases must be wired per directions in drawings).

- Electrical Contractor must install wire guards over lights on 8’-0” ceilings or lower throughout the entire store.

- Electrical Contractor is responsible for replacing and installing all missing power pole trim rings.

- Electrical Contractor to install Aluminum “In Use” receptacle covers when specified or required, plastic covers are not acceptable.

- General Contractor must use Contract Flooring (contact #800-356-6792 or #252-522-4588); Haywood Floor Covering, Inc. (contact #804-824-9741 or #804-815-2295), Tino Tile (contact #704-636-7735), for ALL store soft tile installation.  No other soft tile contractors will be accepted.

- All roof openings due to removal of HVAC or refrigeration equipment shall be patched or repaired in compliance with the roof manufacture’s standards.  General Contractor must verify the existing warranty with the Building's Owner to avoid possibility of voiding this warranty.  Any opening over 12” x 12” requires welded burglar bars in the opening.

- Mechanical Contractor to remove the existing smoke detectors once new smoke detectors are installed (New smoke detectors installed by Food Lion Vendor) and operating.  Electrical Contractor must remove wiring for smoke detectors in HVAC duct being removed (New wiring will be performed by Food Lion Vendor).

- General Contractor is to replace missing or damaged weather-stripping, sweeps and New style carpet thresholds on all exterior doors. (Have Store enter a work order for Automatic door sweeps and weather stripping.)

- General Contractor is to remove all old silencers and install new door silencers on all door frames after painting.

- General Contractor must install through bolts on new/relocated door closures.

- General Contractor must install commercial grade kick down door stops on all interior hollow metal doors.  (except front office inner door)

- General Contractor is to install kick plates on all doors that are missing or damaged.  Do not install on rear dsd/dock door.

- General Contractor shall caulk around all fixtures in restrooms/all corridors/produce prep/meat prep and deli/bakery area and all offices throughout the entire store – and/or accessories, which fasten to the wall.  (Examples:  water fountains, sinks, paper towel holders, electrical plate covers, plumbing fixtures, plumbing escutcheons, electrical outlets, sprinkler escutcheons and wall mounted fixtures, etc.)

- General Contractor must extend the marlite wall finishes above the ceiling grid and attach the grid to the marlite. The marlite is not to be finished to the bottom of the grid.  Marlite applied to exterior block walls shall include 6 mil poly, furring strips, 1/2” Plywood, then marlite.  Interior block walls will require furring strips, ½” plywood, then marlite.  Wainscot application will require ½” plywood adhered to block then marlite.  Coordinate each area with Construction Manager.

- Painting Contractor is to follow the Food Lion National Account Paint program with Sherwin Williams Paint Company. Painting Contractor is to purchase all paint needed for this project (interior and exterior) from Sherwin Williams only.  Painting Contractor is to use the code “National Parent #C137” when ordering paint for this project.

- Painting Contractor is to properly paint Marlite as indicated in plans and bid notes by following the following procedures:  Prepare surface by cleaning Marlite and de-gloss surface using a 3M pad or ultra-fine grit sandpaper.  Fill any holes, cracks, or imperfections with a wood filler or latex based caulk.  Apply prime coat "Shellac Primer BA9W8050 by using natural bristle or nylon/polyester brush, ¼" – ½" nap synthetic or mohair roller.  Next, lightly sand previously primed surface using fine grit sandpaper.  Topcoat is to be 2 coats of "Zero VOC Acrylic B66-650 applied with nylon/polyester brush or 3/8" woven roller.  General Contractor is to verify each step is followed by providing digital photos of steps followed, failure to follow these steps along with pictures will result in new application of entire process at the General Contractor's expense.

- General Contractor is to use the following Marlite product when patching areas due to case/equipment moves prior to painting existing Marlite:  1001-S4 (paintable white with 4" grooves) or 1001-BG2 (paintable white with 2" grooves).

- General Contractor to use "Low Odor" acrylic flooring in areas defined on plans or bid notes.  "Protect 4300 PA" by Protective Industrial Polymers (contact – Steve McCamey 804-937-5000 activatedflooring@gmail.com) – OR – "Accelera HQ" by Dur-A-Flex (contact – Kevin Stephens 919-208-8662 kevins@dur-A-flex.com ).  Electrical/Plumbing/General Contractor shall bid all labor and material to disconnect and re-connect/adjust all equipment and fixtures to complete this flooring installation.

- Sprinkler Contractor to install white semi-recessed sprinkler heads in rooms that get new ceilings. This shall include all labor and material. All sprinkler escutcheons throughout the entire store should be secured to the ceiling. Any rusted heads and/or escutcheons should be replaced throughout the store and all prep areas/ coolers/ freezers/ etc.

- Sprinkler Contractor must install wire guards over sprinkler heads on 8’-0” ceilings or lower throughout the entire store.

- Sprinkler Contractor must obtain Décor drawings, reflective ceiling plans, mechanical drawings, steel drawings, and electrical lighting plans to design the sprinkler system to allow for adequate water coverage as per the fire marshal’s requirements/codes.  Sprinkler Contractor to provide Retail Business Services Construction a Disk containing the drawing file of the plans used.

- In the best interest of our Customers, the following construction activities are limited to “night” work only and should be bid as such (night work is defined as 10 pm until 8 am):  Sales Area Painting, Sales Area Ceiling Tile Replacement/Cleaning, Sales Area Lighting Demo/Installation, Sales Area Framing and Drywall installation, Sales Area Drywall finishing, VCT Demo/Install, Sales Area Mechanical Duct Demo/Install, Sales Area Sprinkler Pipe Demo/Install, Entire Store Saw Cutting or Jack Hammering, Deli Floor and Wall Tile Demo, Restroom Floor and Wall Tile Demo, Restroom Plumbing work, Sales Area Masonry/Framing Grinding/Sawing.  All other dust or noise creating work on the sales floor shall be completed at night.  Any excavation in front of the store for Grease Traps, etc. is to be completed at night.  Coordinate with Construction Manager for approval of any work that would violate this requirement.  Store Manager has authority to halt work that he/she deems unsafe or disruptive to customers.

- General Contractor to replace all transfer fan filters at the end of scheduled work, provide photo of each removed filter to the Construction Manager.

- Any new cable installed will be a Belden 1212 CMR Cat5e 4 pair 24 AWG (Belden 1200 DataTwist Cable Series).  New cables installed by the remodel Electrician are to be Blue in color and labelled using Duct Tape or paper tags.

- Electrical Contractor is not responsible for pulling data cables from any equipment to Next Gen cabinets, these cables will be installed by a Food Lion Vendor and should not be included in the Electrician’s bid for this project.  This excludes items that are not tied to the Next Gen cabinets such as Lotto, ATM, etc.

- All 3rd Party Professional Cleaning as indicated in the bid notes for Deli final cleaning shall be completed by a Professional Cleaning Company approved by the Construction Manager for this project.  The following procedures are to be followed:

- The Cleaning Company will be required to use a commercial grade pressure/steam cleaner and shall follow Food Lions specs on emissions within the building. (No gas or propane equipment within the interior of the building)

- The Cleaning Company will be required to use a commercial grade kitchen degreaser. Safety Data sheets will be required to be available.

- Walls shall be scraped to remove any tape, caulk, and foreign residues.

- Walls shall be sprayed with a degreaser, rinsed, and then wiped down. Steam and pressure washing of the walls will be required as needed. A shield will be required for protection of the ceilings so as not to damage the ceiling tiles.

- Floors shall be sprayed down with a degreaser and use a surface cleaner to remove. Pressure wash/steamer will need to be used in areas of excessive dirt and buildup. Then use a squeegee to remove excess to the nearest drain and follow-up with mop pads to help dry the surface.

- Spray all the stationary equipment with a degreaser and wipe them down to a dry state. This shall include all pieces of equipment within the deli bakery.

- Final requirement is to have the PIC, Superintendent, and Construction Manager to sign off on the work performed and that it has been done in conjunction to the noted requirements above.

- Contractor to cover all equipment not being cleaned to protect from contamination or damage.

- Note: General Contractors are not allowed to self- perform this work without the written permission of the Construction Manager.

Turning Power Off to the Store (Panel Replacement/Additions, Breakers, etc.)

- If power is turned off to the store for any reason, the following steps are to be followed and the General Contractor is responsible for this process.

- Inform Retail Business Services Construction Manager (One-week notice)

- Contact and inform Central Station (704 310 2537).

- Turn off all registers and computers individually.

- Turn off "CR" breaker.

- Turn UPS Switch to "Bypass".

- Turn off input breaker to UPS.

- When electrical work is complete and power is back up, turn breakers on.

- Contact Mike Peoples (336-613-3679) and he will walk you thru restarting the UPS unit as this involves some keystrokes, password, and switching the bypass switch.  If the UPS unit is rewired at all due to the "OW" change out the phasing must also be checked, which Mike can walk the Electrical Contractor thru as well.

- Turn on equipment.  A Manager needs to come in early to verify register function (1) one hour before the store opens.  Validate that all equipment (i.e. registers, workstations, etc.) are functional.  If any equipment fails to power up have the store contact Store Technical Services at 1-888-889-1105.

Safety Notes:

- General Contractor MUST maintain an OSHA approved safety program.

- Electrical Contractor will not be allowed to work on live electrical loads.

- General Contractor is to ensure that no emissions generating equipment is used inside the store - (NO

GAS OR PROPANE EQUIPMENT)

- If it is required that emissions generating equipment must be used inside Food Lion, and if approved by

the Construction Manager, the following guidelines are to be followed as a minimum:

A letter of intent on the Contractor's Company Letterhead must be composed stating:

  - Type of equipment being used and its fuel type (Propane, Diesel, etc.)

  - Location (Store Address) approved for use including dates approved for use.

  - Name of Operating Contractor for equipment.

  - Personal Carbon Monoxide Measuring Device will be worn during operation of emission generating equipment.

  - Level of CO that will be maintained during operation.

  - Ventilation system description along with an illustrated drawing of air evacuation.

  - Verification that equipment has been inspected and certified within the last 6 months to operate within tolerable CO emissions.

----------------------------------------------------------------------------------------------------------------------------------------------

The following are department specific notes, please read thoroughly and coordinate with other store documents.

----------------------------------------------------------------------------------------------------------------------------------------------

Front Exterior

- General Contractor to install 10 new Fire Lane signs (reflective); coordinate type with local governing authorities.

- General Contractor is responsible for hanging a “Changes are coming soon” banner under sidewalk canopy.  (Banner is part of Pre-Construction sign package) Location to be determined by Construction Manager

- General Contractor is responsible to skim coat EIFS material to the nearest architectural element. No skim lines or divots will be accepted.  General Contractor will be required to coordinate the EIFS finish with the Construction Manager prior to ordering the material and installation.  Must be painted as described in plans even if using colored EIFS. This is to cover up the left and right sides where old Deli and Pharmacy sings were previously removed.

- Paint Contractor to repair, prep, prime and paint all exterior metals (including the standing seam metal roofs and visible gutters/downspouts and coping/flashing) Sherwin Williams Enduring Bronze.

- General Contractor is to caulk at sidewalk and around columns at storefront with “NP” type compound.

- Plumbing Contractor is to repair and caulk exterior hose bib(s) on front wall.

- Painting Contractor must repaint all exterior metals to include doors, doorframes, lintels, bollards, shopping center signs, light pole bases, metal access panels.

- Painting Contractor is to paint the alarm box and bell under the canopy.

- Electrical Contractor is to replace 3 exterior receptacles.  New receptacles must have weatherproof cover.  Caulk new and existing receptacles.

- General Contractor is responsible for removing (3) and installing (3) bollards after relocating the Propane Cage per plans.  Make finish repairs to the concrete.

- General Contractor to secure a screen to the sprinkler blow-off.

- General Contractor is to clean & repair front canopy ceiling - several areas show signs of sagging.  Ceiling type is vented vinyl.

- General Contractor to clean ALL light fixtures over front sidewalk

- General Contractor is to install access hatches on both ends of the storefront canopy with a keyed latch.

- General Contractor is to steam clean front sidewalks, storefront masonry, vinyl ceilings, and dumpster pads at end of project (coordinate with Construction Manager), must use hot water.  (Store Manager to sign off on completion).

- General Contractor is to have all storefront glass professionally cleaned after pressure washing the sidewalk at the end of the project (Store Manager to sign off on completion).

- SE Retail to replace the existing store address numbers on the storefront glass with new 6” vinyl white numbers on the top right of the far-right window.  Verify address numbers with Store Manager/Local Fire Authorities. General Contractor to remove existing address #’s and clean/repair existing surface.

- General Contractor is to replace the existing hurricane shutter box with new – construct box out of either PVC or Pressure Treated Lumber (Quality Finish Grade only). General Contractor to install new weather resistant keyed pad lock and latch. Label key tag and hand keys to the store manager to secure in the safe.

Front End/Vestibule Area

- General Contractor should contact Portico directly to coordinate installation date of the Vestibule Carpet.  Portico to remove existing VCT and mastic.  Contact is Bill Long - (877) 285-8899 x305 (or Steve Harrison x304).  NOTE: LEAVE A 5% OVERAGE FOR FUTURE USE.  THE STORE MANAGER MUST ACCEPT AND LOCATE EXTRA CARPET SQUARES to backstock platform.  The automatic doors must also be adjusted to allow for egress break away when installing the carpet tiles, if applicable.  Portico to provide new aluminum thresholds at all locations and anchor with flat head Stainless steel screws.

- General Contractor is to fur the entire store front wall 4” from the vestibule wall all the way over to within the new DMO/Associate Training. This is to allow all new electric and data pulls to be concealed within the wall prior to install new wall panels.

- Painting Contractor is to clean and re-paint (4) automatic door packages.  General Contractor to furnish and install a SS wrap (“U” shaped channel) on both door, not covering the locking mechanism.

- General Contractor is to clean and repair (2) fly fans on the interior of the automatic doors.

- General Contractor to maintain existing Flying Insect Traps (with Glue Boards) in the Vestibule.  Remove temporarily for finishes, do not discard.

- General Contractor is to remove and dispose of the parcel pickup pneumatic hose, bell in vestibule & doorbell chime over the outer office.  Make all finish repairs.

- General Contractor is to replace the vestibule ceiling with new acoustical tile per Food Lion Specs and Electrical Contractor to remove/clean all existing lights and re-install.

- General Contractor is to remove poster hanging system from the vestibule windows.

- Electrical Contractor to remove surface mounted conduit and junction boxes, General Contractor to make finish repairs. All new Electric and Data pulls are to be concealed within the walls.

- General Contractor to install new break metal under windows on both sides/right side/left side of vestibule on the sales area side and vestibule side with new break metal to match existing.

- General Contractor must coordinate with the Store Manager on the night of the front end change out to insure there is adequate room to unload the front-end equipment in the store. If space is limited, the General Contractor will be required to provide a storage trailer on site. The General Contractor must provide a forklift for the front-end equipment removal and be responsible for removal/salvage of all front-end equipment.

- General Contractor to replace the existing marlite within the vestibule with new.

- General Contractor will need to caulk all cash register stands, new kiosk, and cigarette base inside and out and around the customer service counter (closing all voids) to the floor after they have been properly installed, aligned and all of the VCT work has been completed. Use a color caulk that matches the bottom metals on the stands. (Coordinated with the Construction Manager.)

- SE Retail to provide all new plexi-glass sneeze guards and install as required across the front end and customer service areas.

- Mechanical Contractor to relocate temperature sensor as directed by the Construction Manager in advance of Front-End change.

- Electrical Contractor is to provide a general use dirty power duplex receptacle where the Communicator Cabinet is shown on plans for store communicators.  Locate receptacle behind cabinet, GC to cut out back of cabinet as needed for receptacle.

- General Contractor to provide labor to remove the Kiosk Shelving for installation of VCT and shall re-install shelving once tile work is complete.  (Product is to be removed and re-installed by Store Associates or Strategy Specialists)

- General Contractor to provide 4x4 blocks (painted Black) for the Ice Vendor to rest on, these blocks are to be left under the ice vendor after the remodel.

- Electrical Contractor to remove and terminate electrical connections at all old sensormatic control boxes and abandoned alarm panels and/or re-route existing circuits if necessary. General Contractor to make any necessary finish repairs.

- General Contractor to Demo any existing wiring troughs and all cables or hangers across the front end AFTER the Front-End Set is complete. General Contractor to contact Kim Sides or Josh Martin so they can schedule MACRO should there be any existing data cables left to be pulled or terminated.

- General Contractor to demo Floating Ceiling above front end in its entirety - remove all cables and hangers. General Contractor to coordinate the relocation of any: security cameras, strobes or sensors with Jason Pethel. General Contractor to coordinate relocation or replacement of any ac ducts/diffusers with the Mechanical Contractor that fall within the floating ceiling.

- Electrical Contractor to remove existing lights from Floating Ceiling above the front end and temporarily suspend them (even spaced above the same area) until the new High Bay lights are delivered and can be installed. The old lights should be repurposed.

- Mood Audio to replace any speakers in the floating ceiling with new for an open ceiling as per Food Lion Spec’s.

- Sprinkler Contractor to raise any existing sprinkler heads from the Floating Ceiling above the front end. Relocated sprinklers should align AFF with adjacent sprinklers nearest the front end.

- Electrical Contractor to remove the existing pendant lights in front of the vestibule windows and terminate the connections. General Contractor to replace approx., (10) ACT ceiling tiles in this area.

- Electrical Contractor to remove and terminate ALL existing plug mold along the walls.

- Electrical Contractor to relocate ALL light switches so they land above the new Acrovyn wall bumper trim.

Existing Customer Service / Existing Data Server Room / NEW Work Room

- General Contractor and Electrical Contractor to provide demo as required of customer service counter.  Coordinate with Construction Manager. Electrical Contractor is to remove any and all receptacles and communication cabling.  The existing communications CAT5 cables are to be labeled and pulled back to Communications Panel.  (Cut cables will be re-pulled at no cost to Retail Business Services.)

- General Contractor is to fur the store front wall 6” within the new DMO/Associate Training. This is to allow for plenty of space for the installation of the OW & CR panels prior to install new wall panels. (Please refer to my redline mark-up A1.01_B)

- General Contractor to Demo any existing wiring troughs and all cables or hangers, AFTER the Front-End Set is complete and the customer service area has been demo’d. General Contractor to contact Kim Sides or Josh Martin so they can schedule MACRO should there be any existing data cables left to be pulled or terminated and to coordinate the removal/relocation/installation of any equipment.

- General Contractor to contact Mike Peoples to coordinate the relocation of the existing UPS a minimum of 2 weeks in advance.

- Electrical Contractor to include ¾” conduit from OW panel to UPS location and ¾” conduit from UPS to CR panel to eliminate the current wiring outside the office including removal of the JB.  Coordinate with Mike Peoples on the installation of conduit and their work to run power and make connections.

- General Contractor to include labor to revise opening for new safe, height to allow 1 ½” gap, provide painted 1x6 pine wood trim with a 2” trim, relocate security keypad, and rework office shelf.

- General Contractor is to install a 2”x2” angle (width of safe) on the floor behind the safe in the office. Anchor to the floor after positioning safe.  Painting Contractor to prime/paint angle.

- Painting Contractor to hand paint the office safe with a short nap roller, both inside the office and on sales area side. Color to be "Macadamia" SW6142 in a semi-gloss finish on both sides of the Work Room.

- General Contractor to install an aluminum kickplate on the bottom of the existing safe as part of the stainless-steel package to replace the missing safe kickplate.

- General Contractor to install a 2" core drilled bollard (Painted Black or Stainless) where directed by the Construction Manager as a door stop for the safe.

- General Contractor to install new Marlite on all (4) walls within the new Work Room and the Painting Contractor to paint remaining drywall/Marlite walls.  Electrical Contractor to install a quad receptacle @42” a.f.f. that will above the new work room counter.

- General/HVAC/Electrical Contractor is to add a 1400 CFM transfer fan (contact: SESCO/McNamara - 888-996-2220) to the office storage.  Remove any existing HVAC and cap off.  Fan power supply to be tied to lighting circuit for operation.  Duct conditioned air back into sales area. (Min. of 10’ away from office door) Electrical Contractor is to tie power for the fan to the office light circuit, abandon and blank off old switch for fan.

- General Contractor to install all new acoustical ceiling tiles in cash office as per plans & specs once all overhead work is complete.

- General Contractor to install a new hollow metal door and frame, door to be undercut 2” and have louvers.  Painting Contractor to paint the new door/frame.

- General Contractor to add a louver kit in the new door.

- General Contractor is to provide and install a door scope in office door.

- General Contractor to install a kickplate on both sides of the office door at the bottom of the door, also install a 12" kickplate behind the lockset above the louver on both sides of the office door.

- General Contractor is to install (1) new counter @34” AFF and (2) new 14” deep Shelves above in the work room (New Laminate Color is Desert Beige)

- Painting Contractor to paint the underside of the shelves Macadamia SW 6142.

- General Contractor to replace ALL existing wood doors and/ or wood frames (customer facing) with new Hollow Metal doors and metal frames as per Food Lion standard specs per each space/room – this is typical throughout the entire store. Paint color to be Macadamia SW6142

- General Contractor to coordinate the relocation od the safe with Keep Safe.

##### NEW Department Manager’s Office / Associate Training Room

- General Contractor to install new Acoustical Tile Ceiling.

- Electrical Contractor shall install (3) 2x4 Lay In LED fixtures.  Lights are to have a flush mounted wall switch at the entrance. Coordinate exact location of the utilities with the Construction Manager.

- Mechanical Contractor to install a new transfer fan, coordinate the location of the transfer fan with the Construction Manager.

- General Contractor to install all new marlite panels throughout.

- General Contractor is to provide and install (1) new laminated millwork countertop.  Coordinate utilities with counter location!  Counter to be 30" above finished floor, refer to plans for millwork details. Laminate Color to be Desert Beige and underside to be painted Macadamia SW6142

- General Contractor to provide plastic grommets for wiring penetrations of countertop.

- General Contractor to install (1) new laminated millwork shelf mounted 28” above countertop.  Laminate to match counter.

- Electrical Contractor to install one quad receptacle 64” AFF above the shelf on center.

- General Contractor to install a new hollow metal door undercut 2” with a window.

- General Contractor to install push/pull plate hardware on door.

- General Contractor to install new stainless kickplates on both sides of door with a kickdown.

- Electrical Contractor to install (2) additional Convenience receptacles on their own circuit. (Coordinate location with Construction Manager)

Existing Broom Closet

- General Contractor to install new Acoustical Tile Ceiling.

- Electrical Contractor shall install (1) 2x4 Lay In LED fixtures.  Light is to have a flush mounted wall switch at the entrance. Coordinate exact location of the utilities with the Construction Manager.

- Painting Contractor to epoxy paint all (4) walls floor to ceiling – color to be Macadamia SW6142

- General Contractor to install a new hollow metal door undercut 2”.

- General Contractor to install push/pull plate hardware on door.

- General Contractor to install new stainless kickplates on both sides of door with a kickdown.

- Soft Tile Contractor to install new VCT and Vinyl Cove base throughout.

Restroom Corridor

- General Contractor is to replace the ceiling tile in the restroom corridor; new tile to be Armstrong Humiguard.

- Electrical Contractor is to install (3) 2x4 LED “LM” lay-in light fixtures.

- General Contractor to remove existing wall paneling and install new Marlite as directed in plans.

- General Contractor – NOTE: when replacing Marlite in corridor; new marlite is to finish 6” above ceiling.

- General Contractor is to install new “Black” nylon single swing door w/Metal Frame into Deli Prep area

- General Contractor is to install new Black ADA approved restroom placards.

- Plumbing Contractor to install a new ADA approved high/low cooler (Elkay EZSTIL8C Stainless Steel) and provide new water line. Electrical Contractor to install new receptacle for power.

- General Contractor to full stainless steel “Cased Opening” to transition finishes from the sales floor into the corridor (8”-12” wide) w/2” returns minimum. May be necessary to add wall blocking.

- General Contractor to install a stainless steel “Back Splash” behind the water coolers to protect the walls from water stains. This is to be caulked around the top of the water coolers.

Customer Restrooms

- General Contractor to install new hollow metal doors undercut 2” with stainless kick plates and kick downs.

- General Contractor to reinstall “toe pulls” at base of doors as needed or provide new if not in place.

- General Contractor to install new (includes framing) drywall ceiling w/1x trim around the entire perimeter.

- Painting Contractor is to paint restroom ceilings white epoxy.

- Electrical Contractor is to install (4) new “BL” lights parallel with stalls with wall mounted switch. Must install (1) emergency light (“BLE”) in both restrooms. (see specifications)

- Sprinkler Contractor must install white semi-recessed sprinkler heads in the restrooms.

- Mechanical Contractor is to replace the restroom exhaust fan.

- General Contractor is to install new baby changing stations. Follow installation guide rules included with each station and dimensions on approved plans to ensure proper mounting height.  Changing Station is to be "Diaper Depot Horizontal" 2300 (Ivory).

- General Contractor to clean the sinks, urinal, and toilets with pumice stone on ceramic to remove hard water stains.  Remove existing caulking and re-caulk all fixtures.  Replace caulking on changing stations.

- General Contractor is to remove tampon dispensers and paper towel dispensers from restrooms; no holes in walls shall be visible.

- General Contractor to coordinate (rling@newlifetilecleaner.com) with New Life Tile for the installation of the sealer used in the restrooms. This shall include all labor and material associated with the sealer installation.

- General Contractor is to professionally clean all restrooms, complete this work at end of project and must have the Store Manager to sign off on the completion.

- General Contractor to remove all existing wall anchors and grout fill any existing holes in wall tile or grout (color to match)

Deli/Bakery Prep & Deli/Bakery Sales Area

- Electrical Contractor is to provide temporary power to the refrigerated island case by dropping MC cable through the ceiling, install in permanent location after located by the Construction Manager and floor tile work is complete.

- General Contractor to install the Kick Plate supplied with the new Wing Bar once floor work is complete.  Caulk to floor, color to match.

- General Contractor to add an aluminum swinging gate measured and ordered by General Contractor after Deli cases are set and opening size is determined.  Contact Michelle Harrelson with Hefco @     800-327-1817, email: cs1@hefcollc.com to provide dimensions of needed gate.

- Mechanical Contractor is to replace the deli closet exhaust fan.

- General Contractor is to clean and repair ceiling in the Deli Bakery.  Ceiling type is vinyl faced drywall tile.

- General Contractor to replace approx., (30) vinyl faced drywall ceiling tiles.

- General Contractor to clean all light fixtures in the Deli.

- Electrical Contractor to remove light switch from Deli Freezer and hard wire through energy management, install blank cover.

- General Contractor is to provide metal flashing to enclose the top and sides of the rack oven.

- Electrostatic Painter is to electrostatically prep and paint ALL of the metal panel walls and low walls within the deli prep area (Floor to ceiling) this also include Cooler and Freezer walls/Doors and interior closet/storage walls. Color is to be smokey beige.

- General Contractor must coordinate any floor and wall dimension discrepancies with the Construction Manager prior to installation.

- General Contractor to include the application of "Low Odor" acrylic floor coating in the Deli Prep and Cooler.  Refer to "General Note" section for details and ordering information. Electrical/Plumbing/General Contractors to include labor and material to disconnect and reconnect/adjust all equipment and fixtures.

- General Contractor to maintain existing Flying Insect Traps (with Glue Boards) in the Deli.  Remove temporarily for finishes, do not discard.  Vendor (through Food Safety Dept.) will be responsible for replacing units as needed as part of the “Fly Program”.

- General Contractor to refer to finish metals note under “Sales Area” for stainless steel corner guards/caps on exposed tile corners.

- Electrical Contractor to provide a dirty power dedicated circuit to a junction box above the ceiling above the Hot Case for the LED Menu Monitors (circuit cannot be tied to the Energy Management Panel and must have continuous power).  Once the monitors are installed by others, install a duplex flush mounted in the ceiling tile within 6" of the monitor post and run BX Cable from the JB to the receptacle.

- Electrical Contractor to install the 4' LED light centered on the "Taste of Inspiration" sign after installed. Coordinate location with Construction Manager

- Plumbing Contractor needs to clean / level / install ALL sink(s) in the deli and caulk to walls.

- Plumbing Contractor is to install (4) new floor sinks at existing prep sinks.

- General Contractor to install a Deli dust wall during remodel work of deli.

- Electrical Contractor is to provide temporary power from the existing Deli/Bakery scale location to outside of the dust wall.  GC is to provide a place for Deli scale to sit for use during shutdown.

- General Contractor to employ a 3rd Party Professional Cleaning Company to professionally clean the deli once the majority of the work is complete prior to opening the deli, coordinate with Construction Schedule.  Refer to Standard Note section of these bid notes for approved cleaning contractors.

- Plumbing Contractor no longer supplies the mixing valve for the Eye Wash Station, this will be part of the equipment supplied.

- Plumbing Contractor to replace water supply valves and fixture at existing can wash.

- Paint Contractor to paint Deli Closet/Storage Room: walls, door, frame and ceiling White Epoxy per Food Lion specs.

- Electrical Contractor to remove all existing pendant lights throughout the deli area and pull the abandoned circuits. General Contractor to make any necessary finish repairs.

- General Contractor to remove all existing Grease Lines that have been abandoned and infill any openings in the ceiling, wall or floor where the line penetrated. (Exterior Stainless lockable access box/panel can remain)

- General Contractor is to install new “Black” nylon single swing door w/Metal Frame into Deli Prep area from Produce Sales area.

- General Contractor to install (3) new hollow metal doors/frames undercut 2”.

- General Contractor to install push/pull plate hardware on doors.

- General Contractor to install new stainless kickplates on both sides of doors with a kickdown.

- General Contractor to install (3) new ceiling mounted boat racks (coordinate locations with Retail Specialist)

- General Contractor to remove the “Floating Bulkhead décor and décor elements” above the floating ceiling and all the attachment hardware and cables in its entirety.

- Electrical Contractor to remove and terminate all old pendant light ceiling mounts/junction boxes.

- Mechanical Contractor to replace all HVAC diffusers and returns with new as per Food Lion spec’s. throughout the prep area.

- Electrical Contractor to install new the wing bar and R-K Cut Fruit Island on a whip until the final location is marked by operations after new VCT is installed. Then the new Telepole can be installed.

Produce Sales Area

- Sprinkler Contractor to include time and material to identify sprinkler head/trellis interference with local authorities and shall relocate and add heads if required to meet coverage code.

- Electrical Contractor is to provide temporary power dropping MC cable through the ceiling to the left side of refrigerated island cases, install in permanent location in telepole (that accepts internal duplex receptacle) after located by the Construction Manager and floor tile work is complete.  Coordinate with latest fixture plan for quantity of cases and plans for telepole model numbers.  Telepoles are to be mounted to match the angle of the cases and receptacle facing the rear.

- Electrical Contractor to provide Armored Cable (MC) connection from a JB above the ceiling to the electrical connection point of the Bus Strut lighting grid.  Cable to be aluminum color finish and is to be secured to a supporting Bus Strut cable.

- Electrical Contractor to provide weatherproof general use duplex receptacle on column above SS wrap or 48” aff. for produce display cleaning vacuum.

- Plumbing Contractor to make cold water connection to all case mounted quick connects on the Produce Cases.  This to be completed during Produce case work.

- General Contractor/Electrical Contractor to demo all existing ceiling mounted décor elements/canopies/trellis light tracks etc….Sprinkler contractor to make any necessary adjustments as required.

- Painting Contractor/General Contractor to repair, prep, prime and paint all CMU walls all the way up to the deck (there are significant signs of moisture damage)

Produce Prep

- General Contractor is to install teardrop bumpers and door seals on doors into the sales area and into the backroom.

- General Contractor is to clean ceiling and walls in the produce prep.

- General Contractor to re-caulk ALL cooler panel seams (wall and ceiling panels and along the entire base at the perimeter – fill/repair any holes.

- Plumbing Contractor to relocate ½" cold water with ball valve for the misting system as located on the prints or as redirected by the Construction Manager.

- General Contractor to maintain existing Flying Insect Traps (with Glue Boards) in the Produce Prep.  Remove temporarily for finishes, do not discard.  Vendor (through Food Safety Dept.) will be responsible for replacing units as needed as part of the “Fly Program”.

- General Contractor to pressure wash the Produce Prep and Cooler floor.

- General Contractor to install new boat racks– there should be sharpie marks already on the walls within where operations want these installed.

Meat Prep & Meat Sales area

- Electrical Contractor must provide temporary lighting over cases for any bulkhead remodeling. Coordinate with the Construction Manager for reusing the existing light fixtures.

- General Contractor to include saw cutting for electrical conduit between the Island Meat case and the wall cases to allow installation of receptacle on case.  Electrical Contractor to include circuit and standard receptacle with waterproof cover (GFI only if required by Inspector) mounted to base of the Island Meat case closest to the right wall.  Pushing circuit in Seal Tight through existing refrigeration conduit is an acceptable alternative but not always possible.

- Electrical Contractor to replace the meat bell push button with the following:  buzzer plate for meat department to be Edwards #147-1, Stainless Steel with an Edwards #690 push button

- Electrical Contractor to provide and install a 24-volt service bell.  Bell is to be "Edwards #340G5" (4" diameter, gray in color) with no alternates accepted.  The service bell system will require a transformer rating for 120VAC input voltage to 24VAC output voltage and a 24VAC pushbutton.

- General Contractor is to install teardrop bumpers and door seals on doors into the sales area and into the backroom.

- General Contractor to replace the window kits in the existing double swing door going into the Sales Area and into the Backroom.

- General Contractor is to clean / repair ceiling in meat prep.  Ceiling type is Cooler Panel.

- General Contractor to re-caulk ALL cooler panel seams (wall and ceiling panels and along the entire base at the perimeter – fill/repair any holes.

- General Contractor must wipe down and clean the electrical cord drops from the ceiling.  Zip Tie all un-used cord drops to the ceiling.

- Electrical Contractor must seal the light fixtures from the top, so no condensation enters the fixture in the cooler and freezer.

- Electrical Contractor to remove the light switch for the Meat Freezer and install a blank cover, hard wire lights to be controlled by energy management.

- Plumbing Contractor no longer supplies the mixing valve for the Eye Wash Station, this will be part of the equipment supplied.

- General Contractor to install a full stainless wrap around the metal door frame at sales floor entry.

- General Contractor to install a full stainless wrap around the metal window frames at sales floor.

- Paint Contractor to paint Meat Office walls, door, frame and ceiling White Epoxy per Food Lion specs.

- General Contractor/Plumbing Contractor to coordinate all new Pit & Drain locations with the Energy Specialist and Construction Manager.

Sales Area

- General Contractor to replace ALL existing wood doors and/ or wood frames (customer facing) with new Hollow Metal doors and metal frames as per Food Lion standard specs per each space/room – this is typical throughout the entire store. Paint color to be Macadamia SW6142

- General Contractor to include Ground Penetrating Radar inspection and report for the entire perimeter of the sales area prior to saw cutting to install drain system or other underground infrastructure.  GPR report to be provided to Construction Manager.

- General Contractor is to ensure that all trades cleanup after their work has ended for the day or prior to them leaving the area.  This is to include removal of debris along with any needed dusting, sweeping or mopping.

- General Contractor MUST provide a cleanup person who will clean 40 hours per week for 12 weeks as indicated in the Construction Schedule (6) during floor trenching and (6) during VCT floor work.  This cleaning is to include dusting of product and shelving including displays in the entire store for the duration of VCT work and similar duties as required for dust generated by décor removal and wall finishes.  This person shall be identified to the Construction Manager and Store Manager.

- Refrigeration Contractor is to remove all old cases and/or unused equipment and move to backroom roll-up doors or onto salvage trailer for the General Contractor.

- Mechanical Contractor is to replace all Sales Area/customer facing (including deli prep) “large circular diffusers w/new per Food Lion Specs.

- General Contractor is to clean/dust off the sales area open ceiling and clean all HVAC existing diffusers that are to remain in the store.

- General Contractor is to leave 20 ceiling tiles that will be used for Loss Prevention for security cameras, etc.  Ceiling tiles are to match the sales area ceiling tile, place them on the storage platform in the backroom. (for office and the vestibule)

- General Contractor must remove all unused clips from the ceiling.

- General Contractor is to include removal/relocation of sprinkler heads to facilitate construction of new walls or canopies.

- General Contractor is to re-secure/reattach and provide sprinkler escutcheons as required throughout the store.

- General Contractor must verify that the sales area bulkheads are structurally sound to support additional wall loads. Refer to detail in plans for structural repairs if needed.

- General Contractor must submit a letter to Retail Business Services Construction that the existing/remaining bulkheads have been certified that they meet structural and architectural criteria.

- Electrical Contractor shall be responsible for relocating or adjusting the height and location of all fire strobes, exit lights, and emergency lights in the sales area to accommodate the new décor package.  These relocations will need to be coordinated with project Décor Contractor and/or the Construction Manager.

- General Contractor to contact Jason Pethel (by email only and copy Construction Manager, Jason.Pethel@RetailBusinessServices.com) for relocation of Fire Strobes in the sales area to accommodate the new décor package.

- Electrical Contractor is to install ALL new emergency and (8) New exit lights on sales floor.  Exit lights shall be LED Technology.  These fixtures are to be replaced prior to sales area painting, failure to do so will result in repairs at the Contractor's expense.

- Painting/General Contractor is to skim the sheetrock walls where old décor is removed and achieve a “Level 4” finish prior to painting.  GC is to skim all imperfections in all sales area drywall as necessary prior to painting the sales floor walls.

- Painting Contractor to refer back to the “Standard Notes” section of these bid notes for directions concerning the National Account program.

- General Contractor to provide and install 1x4 wood nailer at all perimeter wall shelving.  This will be coordinated with the Reset Team Lead at the beginning of Grocery Reset, all material must be on site at start of Grocery Reset.

- General Contractor is responsible for installing new Fire Extinguisher stickers on all sales area and office Fire Extinguishers once all painting and wall finishes are complete.  New stickers are to be as follows:

•	Fire Extinguisher Signs for Curved Surfaces (including round and square columns) – Provide 18"H x 4"W glow-in-the-dark adhesive sign equal to Condor 469V23 (Grainger item #469V23).

•	Fire Extinguisher Signs for Flat Wall Surfaces – Provide 18"H x 4"W glow-in-the-dark plastic sign equal to Accuform Signs MFXG551GP (Grainger item #9CXE3).

- Electrical Contractor to provide telepole from ceiling to the floor (centered behind the case) for any self-contained case not against a wall.

- Electrical Contractor to install the telepole for the Fresh Pet case to the top of the gondola behind the case, receptacle to be at base of telepole so power cord does not extend above Fresh Pet Case.  If existing fresh pet case, provide power same day as relocated.

- General Contractor must remove insulation from the walls and ceilings where necessary.

- Plumbing Contractor is to install a new High/Low ADA compliant water cooler in the sales area per Food Lion specs

- General Contractor is to include the material and installation of all Finish Metal work required.  Acceptable standards are:

  - 18-gauge Stainless Steel, #3 Finish, non-hemmed edges (PVC coated) on all exposed corners across the storefront, boxed column wraps are to be 22-gauge, #3 Finish Stainless Steel.

  - 11-gauge Stainless Steel, #2B Finish (PVC coated) thresholds at all Deli openings, Meat Prep to Sales Area opening, Produce Prep to Sales Area opening, and any Sales Area to backroom opening or where there is a hollow metal framed door or window. Stainless is to return all the way back to the frame.

  - 18-gauge, #3 Finish, Stainless Steel with non-hemmed edges (PVC coated) 4' corners on all outside Deli Hard Tile corners.

  - 20-gauge, #3 Finish Stainless Steel (PVC coated) for all Oven and Hood Flashing.

  - 18-gauge, #3 Finish Stainless Steel (PVC coated) for all Kickplates.

  - 18-gauge, #3 Finish Stainless Steel (PVC coated) 4’ corner guards on all sales area exit door openings, Produce Prep door opening, and Meat Prep Door opening.

  - 18-gauge, #3 Finish Stainless Steel (PVC coated) Restroom Corridor opening wrap that wraps 2” on the sales area side, through the opening and wraps 2” on the Corridor side to create a full cap.

  - 18-gauge, #3 Finish Stainless Steel (PVC coated) 4’ corner guards on any Restroom Corridor exit door openings, restroom door openings, backroom traffic door opening, and any other Restroom Corridor door openings, include an 18 gauge, #3 Finish, Stainless Steel with non-hemmed edge 4’ corner on any outside wall corner in corridor.

  - Cooler/Freezer door(s) in the Deli prep area are to get diamond plate aluminum 4’ A.F.F.  (customer facing only).

  - 18-gauge, #3 Finish Stainless Steel kick plate the length of the rear load dairy coolers front and sides.

  - Deli Prep Cooler/Freezer walls are to receive new diamond plate aluminum that shall extend 48” up wall.

  - Wing Bar base to be 3” SS wrap with ¼” flare at the floor.  Must be caulked to the floor and screwed to the Wing Bar. (If vendor supplied floor trim can’t be located)

- General Contractor is to replace/install 22-Gauge, #3 Finish stainless steel (PVC coated) column wraps 4’ above finished floor on (8) sales area columns that are missing, damaged, or will become exposed as result of shelving changes.

- Electrical Contractor must not install up lighting until after the décor is installed.

- General Contractor is responsible for demo of existing fillers and wedges shown to be removed prior to the Décor Vendor's arrival and case painting.

- General Contractor shall be responsible for removing and disposing of the old valence to include brackets from the cases.

- General Contractor needs to caulk around all doorframes.  This is after all the VCT work has been successfully completed.  The color of the caulk needs to be coordinated with the Construction Manager.

- General Contractor is to install plywood caps over all gaps between shelving the length of the shelving and in gaps between angled cases.

- General Contractor to provide temporary bracing between back to back shelving to cases during case work, Construction Manager to coordinate with Grocery Reset for permanent bracing (or will be handled during Grocery Reset).

- General Contractor to remove sign headers from Lunch Meat, Dairy, and Beer cases.

- General Contractor to remove debris and broom sweep tops of all cases at project completion.

- General Contractor to seal with rodent proof material the drywall to the block wall behind all new and relocated cases where horizontal framing/furring is not present.

- Soft Tile Contractor is to include the use of Mapei "G21" two-part urethane adhesive when placing VCT in front of the Produce Cases planned to contain a misting system.  This adhesive is to be used for all VCT under the case to a minimum of 4' away from the case.

- Soft Tile Contractor is to include moisture test, grinding of any loose patch/high spots/problem areas, sanding entire floor, installation of APAC "V-Block" (or North American "Vapor Guard Pro"), floor patch and leveler, and final sanding in the VCT bid, no change order will be accepted for floor patch.  (refer to specifications for material and products to use)

- Soft Tile Contractor is to include material and installation of VCT under Grab N Go shelving (around the tobacco kiosk) and any perimeter wall shelving that is not attached to the wall.

- Electrical Contractor to include making electrical connection to the Soft Tile Contractor's pigtail for grinding equipment.

- General Contractor to include labor to relocate any shelving not secured to a perimeter wall and Grab N Go shelving (around the tobacco kiosk) for the installation of VCT.

- General Contractor to scrape and sweep clean any VCT that becomes exposed due to the relocation of equipment or shelving. This shall be done prior to opening the store for customers.  Must provide own scrape blade for shelving moves.

- General Contractor shall patch and repair floors due to removal of floor stubs, existing walls, etc.

- General Contractor to include installation and material of temporary VCT when shelving/cases/displays are removed exposing areas of concrete floors that create customer trip hazards.  VCT can be any color.  Applicable if area is exposed for more than one week.

- Plumbing/General Contractor to install 11 new adjustable floor clean outs (Sioux Chief only) as described in plans.  This work must be complete PRIOR to VCT replacement.

- General Contractor/Plumbing Contractor will be required to cut down the 4" hub bells to be ½" above finished floor when installing new 4" hubs or per local jurisdiction requirements.

- General Contractor shall be responsible for installing McCue corner guards as shown on the fixture plan.

- Retail Business Services will provide inspection and jetting of all waste lines.  General Contractor must have all clean out access points open and clear of any construction debris.

- Electrical Contractor must run independent electrical conduit; NO electrical lines are to be run inside the refrigeration PVC chases with refrigeration circuits. (except receptacle for sampling station in first meat promo)

- General Contractor is to ensure that NO plumbing hubs/drains or electrical junction boxes remain behind any void area in the sales areas.

- Retail Business Services will be responsible for handling the gondola mover for the sales area. Number of full moves required 1.

- General Contractor is to provide refrigeration, evac and electrical chases/access panels and finishes for all drops throughout the entire store. Where applicable – coordinate with Energy Specialist and Construction Manager.

- General Contractor to wipe clean all sales area emergency lights and exit signs prior to the completion of the project after all major sales area work is complete.

- General Contractor to clean the top of all floor clean outs in the sales area after all floor tile work has completed at the end of the project.

- General Contractor is responsible for verifying that all circuits (lights, fans, anti-sweat) are wired correctly prior to the Electrical Contractor leaving the store the morning following case moves\installs prior to product being placed in cases.

- Electrical Contractor to label ALL lights, fans & anti-sweats with painter’s tape and a sharpie in bottom right corner of all new or relocated cases. NO exceptions

- General Contractor will be responsible for the disposal of removed refrigerated cases on this project.  The Refrigeration Contractor will move the cases to the dock door, it will be the responsibility of the General Contractor to remove the cases from the building (include removal equipment) to the planned means of removal (dumpster, flatbed truck, etc.).  This does not include any equipment, just cases.  Coordinate with Construction Manager.

- General Contractor to install a new stainless backsplash behind water fountains.

- General Contractor to install Ram Board (held in place with Gorilla Tape) under old gondola locations and after case moves where there is exposed slab/dirty or damaged tile left behind until the new VCT is installed. Estimated 1,500 sq. ft.

- Electrical Contractor responsible for removing all existing telepoles, conduits, receptacles and terminate electrical connections from Gondolas/Shelving on the sales floor PRIOR TO Grocery Reset. Coordinate the relocation/installation of Telepole/power for Fresh Pet with the fixture plan and Construction Manager.

- General Contractor to demo old décor (coordinate any items in question with the Décor Plan and/or SE Retail directly) and make finish repairs to walls (this includes areas in disrepair/moisture damage, cracks, holes etc…) prior to new paint and décor being applied/installed. TYPICAL throughout the entire sales or other customer facing/visible areas. Do NOT discard: Manager Boards/ Story Boards/ TOI Signs/ Aisle Markers or Street Signs. GC will be responsible for replacing any lost items that were to be kept.

- Soft Tile Contractor is to bid using Armstrong Raffia Stream – Earth 55926 12”x24” VCT for ALL full floor replacements.  The new 12”x24” tile should be installed in a stacked pattern.

- General Contractor is to remove the entire EVAC system from walls and ceiling on the sales floor (everything considered to be Visible to the customer.

- General Contractor to include Ground Penetrating Radar inspection and report for all areas with new main lines and Drains/Pits (This must include all slab areas to be cut/trenched) for any new drain lines, pits, drains cleanouts or any other underground infrastructure).  GPR report to be provided to Energy Specialist & Construction Manager. The slab is to be marked-up, reviewed and approved by the Energy Specialist and Construction Manager prior to any slab cutting.

- General Contractor/Plumbing Contractor is to trench up to (within 12”) of all existing and/or relocated cases and install a P-Trap where a new hub drain is to be installed this is ONLY WHERE the Evac system is being removed. The actual hub drain will be cut-in/installed the night of the case move/install as per the construction schedule. (General Contractor to ensure any necessary inspections occur as needed to maintain the schedule). Coordinate with the Construction manager / Energy Specialist. Any existing case that is not being removed/relocated will require the drain to be cut-in (chiseled) beneath the existing case front rail/frame – this is to avoid having to pull the case.

- General Contractor is to Sand smooth at exposed concrete slabs for all trench work.

- Electrical Contractor will be required to relocate the control wiring for the refrigeration circuit EPR from current location to top of cases or where required by the Energy Specialist for ALL new and relocated cases/circuits. This wire will need to be stranded wire ran in rigid conduit to junction box within 2 ft of EPR. If this is a new refrigeration circuit this wire will need to run from refrigeration rack to location of new circuit EPR valve. The Refrigeration Contractor will make final connection in the refrigeration rack and at the EPR valve with wire ran in poly tuff to the solenoid coil.

- The Refrigeration Contractor shall be responsible to re-pipe all existing case drains to the NEW floor drains. The Refrigeration Contractor is also to remove the existing Evac drains under the case. The General Contractor will be responsible for removing the remaining PVC pipe behind the case and overhead.

- Note: All existing shelving will be salvaged to possibly be reused at other stores throughout the year due to supply chain shortages. (SAS will handle all removal, palletizing and shipping of the existing shelving.)

- Electrical Contractor to disconnect and reconnect electrical circuit at existing/new case top fans. Refrigeration Contractor is responsible for the installation of new back-to-back case top fans

##### Grocery Storage Area

- General Contractor to clean the spider webs from the bar joists in the truck dock, grocery storage, and mechanical rooms.

- General Contractor shall be responsible for repairing and replacing all damaged/missing welded wire, doors and framing above all coolers, freezers, and rooms in the grocery storage area…coordinate repairs with HVAC work.  (Allow access to equipment)

- General Contractor to patch all openings in masonry/drywall demising wall and mechanical room created as a result of this remodel project.  Use rodent proof material.  Refrigeration Contractor to fill/seal all new penetrations created under the RC scope of work.

- Electrical Contractor is to make sure all open junction boxes, control panels, and electrical panels throughout the store above the coolers and freezer, above the lay-in ceilings are closed up prior to the project completion.

- General Contractor is to remove the construction debris from the tops of all walk-ins and rooms and sweep clean.

- General Contractor to construct a back-stock storage platform.  Platform to be constructed of ¾"x4x8 plywood with 2x4 supports (turned tall) with six threaded rod passing through the plywood and 2x4 with washer and two bolts supported by unistrut attached to the roof joist.  Coordinate location with Construction Manager, Placement should be above a cooler/freezer top with 4’ clear walkway around and adequate access through perimeter screen.

- Plumbing Contractor is to provide and install check valves on the cold-water side of all mixing valves if not existing to include all prep sinks with hand sprayers and misting system.

- Sprinkler Contractor to repair all holes in ceiling of the Storage Freezer.

- Electrical Contractor to remove the light switch from the Storage Freezer and install a blank cover, hard wire lights to be controlled by energy management.

- Sprinkler Contractor to repair all holes in the Ice Cream Freezer.

- Electrical Contractor to remove the light switch from the Ice Cream Freezer and install a blank cover, hard wire lights to be controlled by energy management.

- Sprinkler Contractor to repair all holes in the ceiling of the Dairy cooler.

- Painting Contractor must paint the grocery storage columns up to the bottom of the bar joist and paint traffic yellow 4’-0” AFF.

- Painting Contractor to paint all backroom and prep-room areas that are painted.  Paint previously painted surfaces, doors, doorframes, etc. in backroom and grocery storage.

- Electrical Contractor to provide power for the (2) new bug zappers in the backroom.  Do Not remove, relocate, unplug, or discard the Flying Insect Traps (with Glue Boards).  Construction Manager to order new/replacement units.

- General Contractor to assemble and install:  Recycle bins, janitor’s cabinet, misc. tables, ALL trashcans, lounge furniture, office furniture, etc.  Coordinate with Construction Manager.

- Tile/General Contractor to install 2” min. flat stock aluminum threshold at all VCT transitions.

- Painting Contractor to include painting the white rodent stripe on the perimeter of the backroom storage area.

- Vendor to replace (2) existing ‘Residential Style” Garage Door(s) at Truck Receiving Bay with new Overhead Door Roll Up style doors per Food Lion Specs. General Contractor to coordinate installation with Vendor.

- General Contractor to coordinate the delivery of the new Trash Dumpsters with Jeff Osborne (704) 314-6410 for when the dumpster enclosure is complete and ready for use.

- General Contractor to instruct the store to stop using the existing trash compactor once the new dumpsters are installed and ready for use. (GC to Post signs and rope off the old compactor loading area within the store) Jeff Osborne to coordinate having the existing trash compactor emptied for the final time and arrange for the compactor to be picked up for salvage.

- Electrical Contractor to immediately disconnect the existing Trash Compactor and terminate all connections. Remove and dispose of any remaining unused hardware.

- General Contractor to infill existing trash compactor opening in exterior CMU wall and paint to match adjacent exterior & interior wall surfaces respectively.

- General Contractor to remove/demo existing trash compactor stair landing and make any necessary surface/finish repairs to the walls and slab.

##### Rear Stair Well/ Upstairs Lounge/ Offices and Restrooms

- General Contractor to replace the existing ACT ceiling tile with new and Electrical Contractor is ro repair or relamp (3) 2x4 lay-in light fixtures.

- Painting Contractor is to prime and paint all metal railings/stair runners and treads.

- Painting Contractor is to paint all walls/doors and frames color to be Macadamia

- General Contractor to clean all areas

- General Contractor to relocate all existing Lounge Equipment and Furniture that is to be re-used to the new Lounge.

##### Mechanical Room

- Electrical Contractor to lower the lights in the motor room so they are under the refrigeration runs. Add light cages to protect lights.

- General Contractor shall leave a set of as-built construction drawings in the mechanical room at the end of the project.  These are to be in a 6” PVC sleeve with threaded end caps and the final completion date written on the PVC sleeve mounted horizontally on the wall.

- Electrical Contractor to add a general use receptacle to the left of the roof access ladder.

##### Janitor’s Area

- Painting Contractor is to epoxy paint the walls around the janitor’s room.

- General Contractor to clean this area thoroughly including pressure washing the existing can wash.

Unisex Employee Restroom

- Painting Contractor is to epoxy paint the walls and ceiling.

- General Contractor is to thoroughly clean. Use pumice stone to scrub sink and toilet. Replace Toilet seat.

- Painting Contractor is to sand, prime and paint the Door & Frame

##### New Lounge – Build as per the plans

- General Contractor is to install (2) new pipe bollards at the outside corners for protection.

Rear Exterior & SidesFloaton

- General Contractor is to provide ample lighting for rear/side of the building container storage.  (Coordinate with Retail Business Services Construction Manager) This area is to be used for job trailers, materials, lifts and other construction needs.  GC is to repair all damage prior to leaving the job.

- General Contractor is to properly re-stripe truck guide stripes (as per Food Lion Plans and Specifications).  Provide glass beads for stripping.

- Electrical Contractor to replace (2) light fixtures over Dock doors. Fixtures are National Account.  Verify type with Construction Manager prior to ordering. (Use 8’ LED “XL” fixtures)

- General Contractor is to re-stencil the store numbers on the back-dock doors and roll-up doors.

- General Contractor is to caulk the joints at the truck pad and the rear walls.

- General Contractor shall install a pull handle on the designated construction door for the remodel.  This door must remain closed for security and should never be propped open.

- General Contractor is responsible for all damaged landscaping, out parcels and finishes around the perimeter of the store due to the construction work. The General Contractor will be required to repair all damaged materials, out parcels, & ruts prior to finishing the job. These areas must be smoothed out, seeded and straw installed.

- General Contractor will not be allowed to pull drop cords thru any hollow metal door which would keep the doors from closing. Coordinate with the Construction Manager for allowable cord location.

- Painting Contractor must repaint all exterior metals to include stairs, canopy supports, doors, doorframes, bollards, light pole bases, etc.

- General Contractor to secure a screen to the sprinkler blow off.

- General Contractor to coordinate the delivery of the two new Trash Dumpsters with Jeff Osborne (704) 314-6410 when the dumpster enclosure is complete. (Minimum 2-week notice)

- General Contractor to instruct the store to stop using the existing trash compactor once the new dumpsters are installed and ready for use. (GC to Post signs and rope off the old compactor loading area within the store and lockout the hatch/door) Jeff Osborne to coordinate having the existing trash compactor emptied for the final time.

- Electrical Contractor to immediately disconnect the existing Trash Compactor and terminate all connections.

- General Contractor is responsible for disposing of the compactor and all of its components.

- General Contractor to infill existing trash compactor opening in exterior CMU wall and paint to match adjacent exterior & interior wall surfaces respectively.

- General Contractor to remove/demo existing trash compactor stair landing and make any necessary surface/finish repairs to the walls and slab.

- General Contractor is to replace the existing Chain Link enclosure w/gate in its entirety just outside of the DSD Door.

- General Contractor is to repaint the existing ramp railing and fill/level all off all upright hand rail posts. Paint Contractor to sand, prime and paint the entire railing.

- Genera: Contractor to replace the canopies above (2/both) dock doors with new as per food lion specs

- Paint Contractor/General Contractor to scrape/repair and fill CMU base of exterior Coolers/Freezers prime and paint.

- General Contractor to repair cracks in ramp surface and spray all weeds with roundup.

- General Contractor to replace rusted access panel at rear ice cream/storage freezer – prime and paint to match.

CC:	Construction Manager – Jon Hart

General Contractor – Sumwalt, Omega, KMD, STH

Energy Team Member – Mike Cochran

Construction Coordinator – Shannon Cheeseman

Ref: 2839walk/sfc

7/27/22

---------------------------------------------------------------------------------------------------------------------------------------------

###### IMPORTANT – Bid Note Attachments

---------------------------------------------------------------------------------------------------------------------------------------------

  - Note: 2019 Case Drains

Store: 2839 Beaufort, SC

Landlord Repair Checklist

IMPORTANT NOTE: All Landlord items listed must have pictures. These pictures must be sent to the Landlord Maintenance Department. – Attn: Vanessa Simerson & Monica Fluke

- Landlord shall make repairs to the roof system as indicated in the roof survey and as indicated by visual inspection.

- Landlord to restripe just across the front of the Food Lion store front parking lot including directional arrows and lane designation in drives and aisles the full length of the Food Lion store front.

- The Street monument sign has some EFIS/trim damage and needs a little cleaning up.

- Landlord shall scrape off all loose paint, block fill, then paint with an elastomeric paint the exterior rear and sides of Food Lion.

- Landlord shall remove weeds and install Pine Needles or mulch in landscaped areas, replace dead/missing plantings in landscaped areas.  Landlord shall plant grass in bare area located

Supermarket Environment Services Co.

P.O. Box 667

Kernersville, N.C. 27285-0667

EMS REMODEL NOTES

FOR ELECTRICAL AND MECHANICAL CONTRACTORS

These notes are provided to clarify the portion of this project.  If there is a conflict between these notes and the print these notes take precedence over the print.   If there are any questions regarding the intent or scope of these notes, please contact Bill McCollough at SESCO (336-580-0152) or billy.mccollough@SESCOhvac.com.

ELECTRICAL:

- Each refrigeration circuit will have its own electrical circuit.  As an example, if one refrigeration circuit is removed and is replaced by two refrigeration circuits an additional electrical circuit will be required.  This circuit will have lights and fans separated and anti-sweat ran through the anti-sweat controller for all new and relocated glass door frozen food cases.

- All refrigerated case lights will be on load six.  Existing cases do not apply, although if an existing electrical circuit is re-used for new cases and or relocated cases the lighting circuit will need to be on load six.

- If a case(s) requires an anti-sweat circuit and the existing wiring does not have this available, then an additional circuit for anti-sweat will be provide and ran through the anti-sweat panel.  EC needs to label all new circuits with both breaker and refrigeration circuit identification.

- If the frozen food line up has changed locations the anti-sweat humidity sensor location must be relocated.  Contact the Energy Team member or your EMS representative for location.

- All new and existing walk-in cooler and freezer lights are to load 1.  Ensure that freezer lights and heater are not on the same circuit.  Deli walk-ins can be load 1 or 4.  EC to furnish contactor(s) if needed.

- If the vestibule has been re-worked in such a manner that the inside lights have now become the outside canopy lights, these lights will need to be relocated to load three.  If outside lights have now become inside lights these will need to be on load 1.

- If a seafood steamer hood is installed an interlock control box will serve as a way of running the hood during the steaming process.  Power for the steamer and control power for the hood exhaust fan is routed through this control box.  The control power for the exhaust will be routed through a load 1 contactor prior to feeding this control box.  See the attachment for detail.  The control box will be supplied by SESCO to the mechanical contractor and is to be wired by the electrical contractor.

- All new grid/track lighting will be required to be two circuited with both circuits on EMS load 1.  Addition contactor(s) may be required and supplied by EC.

- All accent lighting (wall wash, decor or up lights) will be on load 14.  In an older store there may not be a load 14 in which case the EC will wire to load 6.  Coordinate with SESCO.

- EC responsible for providing communication cable for all refrigeration controllers and the HVAC controller.  This will be in the form of CAT5 cables for each controller with stores that have E-2 controllers, or 4 wire shielded cable with stores that have earlier versions of CPC controllers.  Coordinate with the SESCO representative for this store.  You can contact SESCO at 336-996-2220.

- If De-Strat fans are used, they are to be wired through load 1 contactors.  EC to furnish contactor(s) if needed.

- Any additional back room lighting (offices, restrooms, machine rooms etc.) shall be broken through load 1 contactors.  EC to furnish contactor(s) if needed.

- All new and/or reworked EBU lighting and night lighting shall be on a switch free circuit.  If the existing wiring is on EMS it will need to be moved to either the EBU circuit or night light circuit.

- For any store receiving a fire alarm upgrade.  EC shall provide conduit and two 14 AWG wire for fire alarm contact interface relay with ECP.  The two 14 AWG shall be able to reach entire ECP and labeled “Fire Alarm”.  Contact should be within four feet of ECP whenever possible.  Termination by others.

- Electrical contractor is responsible for conduit required by mechanical contractor.  BX or free air cable is not allowed.  Sensor and control wiring cannot be in same conduit. Needs to be completed in a timely manner. Coordinate requirements with MC.

- Electrical contractor needs to install and wire CT’S for the cooking equipment under the kitchen hood.  The control wiring for the CT’S will be taken from the hood control panel terminals H1 and IO1 (2 #14) and wired in parallel so that the hood fans run with the equipment.  Contact SESCO parts for the number of CT’S required keeping in mind that one CT can be used on more than one piece of equipment depending on wire size.  Contact SESCO Commissioning with any questions.

- If EC is reusing existing circuits for either control or power for the hood fan(s) he shall ensure that neither is connected to load 4.

- In all high spend stores the EC is to physically remove the Lite Miser and have it ready to be shipped back on the salvage truck.

- All new 2X4 lay in fixtures at the deli sales area need to be added to the load 1 energy management control. EC to furnish contactor if needed.

MECHANICAL:

- All control wiring provided by the mechanical contractor is to be 14 gauge stranded. BX cable is not allowed. All shielded cable is to be 22 gauge or larger.  All wiring shall be in conduit provided by electrician.  Sensor cable cannot be in the same conduit with controls.  Terminations for the mechanical controls by mechanical contractor.

- If prints call for re-wiring of existing fans in motor room the MC is responsible for providing motor starter for three phase fans or contactors for single phase fans if no starter or contactor is existing.  New machine room fans that require a starter or contactor shall be provided by MC if not already provided by SESCO.

- For stores that are receiving fire alarm upgrade the MC will be responsible for removing all old smoke detectors. Once system has been switched over to fire alarm contact, SESCO will notify GC in writing. MC will then remove old detectors. Wiring from detectors is to be removed to associated junction boxes and capped off with wire nuts. Wiring from ECP terminals is to be removed to trough and capped off with wire nuts.

- If the produce prep thermostat is being replaced with a temperature sensor that is wired back to the ECP, the MC will daisy chain the sensor cable from the ECP over to the appropriate refrigeration rack.  Termination by others.

Fire Alarm Note:  For stores that are receiving fire alarm upgrade the fire alarm contractor is to install, power, and monitor all new smoke detectors for all AHU’S and RTU’S.  Contractor is to provide a relay enclosed within four feet of the ECP and controlled by fire panel.  Contact will be wired by SESCO.  Existing (old) smoke detectors will remain in place until SESCO switches system over to fire alarm panel. Refer to M1.01.

Note – The energy load pattern in table A below is typical of most Food Lion stores built prior to 2005.  Table B is representative of Food Lion stores built since 2005.

Table A

Load 1 – Work Lights				Load 5 – Store Front Sign

Load 2 – ½ Sales Lights				Load 6 – Case Lights

Load 3 – Security- Outside Canopy Lights 	Load 7 – Water Heaters

Load 4 – Deli Lights & Hood Exhaust		Load 8 – Parking Lot

Table B

Load 1 – Work Lights				Load 5 – Sign Lights

Load 2 – ½ Sales Lights				Load 6 – Medium Temp. Case Lights

Load 3 – Security – Outside Canopy Lights	Load 7 – Low Temp. Case Lights

Load 4 – Deli Lights				Load 8 – Parking Lot

Load 9 – Produce & Wine Track Lights		Load 13 – RT & LT Up Lights

Load 10 – Machine Room Exhaust Fan		Load 14 – Rear Up Lights

Load 11 – Machine Room Supply Fan		Load 15 – Parking Lot Security

Load 12 – Water Heaters			Load 16 – Beer Case Lights

Revision 10 May 22, 2018