## Remodel Rack A
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy. |  |  |  | Location: | Beaufort, SC |  |  |  | Rack Model: | Existing HP Rack A | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2839 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/27/21 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | AK-SC255
[11 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA | [6 empty] | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 600
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs |  | Liquid | Suction | Run | Horiz | Riser | Horiz
[6 empty] | Loop MT-1 | [7 empty] | 0 | 0 | 0 |  | 1 3/8 BV | 3 5/8 BV
1 | 4 Doors | RM |  |  |  | Beer/Wine 64 | 3.7 | 27 | Off Cycle | 2.8 | 115 | 2.42 |  | 322 | 278.3 | 0 |  | Solenoid | SORITPI27
2 | 56' | D5LE |  |  |  | Beer/Dairy Doors 59-63 | 28 | 30 | Off Cycle | 9.8 | 115 | 7.18 |  | 1127 | 825.7 | 0 |  | Solenoid | SORITPI411
3 | 12' | LN |  |  |  | Dairy Promo 52 | 4.68 | 20 | Off Cycle | 0.6 | 115 |  | 0.94 | 69 | 0 | 108.1 |  | Solenoid | SORITPI27
4 | 72' | D5LE |  |  |  | Dairy Doors 56-58 | 36 | 30 | Off Cycle | 12.6 | 115 | 9.24 |  | 1449 | 1062.6 | 0 |  | Solenoid | SORITPI411
5 | 8' | D5LE |  |  |  | Dairy Doors 51 | 4 | 24 | Off Cycle | 1.6 | 115 | 1.02 |  | 184 | 117.3 | 0 |  | Solenoid | SORITPI37
6 | 540 sq.ft. | HC8A-372BBALT |  | EXISTING |  | Dairy Cooler | 33.5 | 25 | Off Cycle | 12.6 | 115 |  |  | 1449 | 0 | 0 |  | Solenoid | SORITPI411
7 | 20' | D5LE |  |  |  | Dairy Doors 49,50 | 10 | 22 | Off Cycle | 3.5 | 115 | 2.56 |  | 402.5 | 294.4 | 0 |  | Solenoid | SORITPI37
8 | 8' | D5LE |  |  |  | Dairy Doors 48 | 11.4 | 24 | Off Cycle | 1.6 | 115 | 1.02 |  | 184 | 117.3 | 0 |  | Solenoid | SORIT PI27
9 | 36' | D5E |  |  |  | Lunch Meat 44-46 | 53.1 | 24 | Off Cycle | 6.3 | 115 | 3.08 |  | 724.5 | 354.2 | 0 |  | Solenoid | SORITPI49
10 | 48' | M3 |  |  |  | MD Meat | 53.8 | 18 | Off Cycle | 8.4 | 115 | 9.2 | 0 | 966 | 1058 | 0 |  | Solenoid | SORITPI49
11 | 19x28 | HC6E-156 |  | EXISTING |  | 1/2 Meat Cooler (L) | 14.77 | 20 | Off Cycle | 4.4 | 208 |  |  | 915.2 | 0 | 0 |  | Solenoid | SORITPI37
12 | 19x28 | HC6E-156 |  | EXISTING |  | 1/2 Meat Cooler (R) | 14.77 | 20 | Off Cycle | 4.4 | 208 |  |  | 915.2 | 0 | 0 |  | Solenoid | SORITPI37
13 | 28' | M1 |  |  |  | SD Meat | 15.3 | 18 | Off Cycle | 3.5 | 115 | 0 | 0 | 402.5 | 0 | 0 |  | Solenoid | SORITPI27
14 | 600 sq.ft. | 2)GAL36-135 |  | EXISTING |  | Meat Prep | 39 | 30 | Off Cycle | 9.6 | 115 |  |  | 1104 | 0 | 0 |  | Solenoid | SORITPI49
15 | [5 empty] | Subcool LT | 93.22 |  | none |  |  |  |  | 0 | 0 | 0 |  |  | ORIT 20
16 | [5 empty] | Future | [7 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing HP Rack A |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCXV8412
Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 15.1
Outside Air Temp. |  |  | 100 | 1 | 1 | 3DB3R12ME-TFC | 90.3 | 15 | 10 |  | 43.6 |  | 3DB3R12ML-TFC |  |  | 0 | 60A | 50A | #6 | F P I |  | 12
Required Load Group 1 |  |  | 415.24 | 1 | 2 | 3DF3A120L-TFC | 105 | 15 | 12 |  | 48.2 |  | 3DF3R15ML-TFC |  |  | 0 | 70A | 50A | #4 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 594.3 | 1 | 3 | 3DS3-150L | 107.5 | 15 | 15 |  | 59.6 |  | 3DS3R17ML-TFC |  |  | 0 | 80A | 60A | #4 | FLA |  | 32
Effective capac. with subcooling |  |  | 594.3 | 1 | 4 | 4DA3-200L | 127 | 15 | 20 |  | 66 |  | 4DA3R18ML-TSK |  |  | 0 | 90A | 75A | #3 | MCA |  | 35
% Excess Capacity Group 1 |  |  | 30.13% | 1 | 5 | 4DK3R22ME-TSK | 164.5 | 15 | 25 |  | 82.2 |  | 4DH3R22ML-TSK |  |  | 0 | 125A | 90A | #1 | MOPD |  | 40
Rej. Heat (MBH) Group 1 |  |  | 820.134 | [16 empty] | Weight |  | 2880
|  |  | 0 | [16 empty] | Size |  | 96x220
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 8
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2 1/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2 1/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-9108 |  | Drain Regulator | [5 empty] | Air reclaim |  | 16D17B |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 820.134 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 410.067 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 49.525 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs.

## Remodel Rack B
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy. |  |  |  | Location: | Beaufort, SC |  |  |  | Rack Model: | EXISTING HP RACK B | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2839 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/27/21 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
[11 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA | [6 empty] | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 400
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
[6 empty] | Loop MT-2 | [7 empty] | 0 | 0 | 0 |  | 1 3/8 | 3 1/8 & 2 5/8
1 | 4 Drs | RM |  |  |  | Deli BB 5 | 3.7 | 27 | Off Cycle | 2.8 | 115 | 2.42 |  | 322 | 278.3 | 0 |  | Solenoid | SORITPI27
2 | 6' | PF |  |  |  | Cold Deli 6 | 8.5 | 22 | Off Cycle | 1 | 115 | 2 |  | 115 | 230 | 0 |  | Solenoid | SORITPI27
3 | 12' | BMD |  |  |  | Service Deli 4 | 6 | 22 | Off Cycle | 1 | 115 | 2.4 |  | 115 | 276 | 0 |  | Solenoid | SORITPI27
4 | 12/24' | PT/BX4LP |  |  |  | SS Deli 1-3 | 23.6 | 22 | Off Cycle | 2.1 | 115 | 5.4 |  | 241.5 | 621 | 0 |  | Solenoid | SORITPI27
5 | 12' | PTD |  |  |  | Service /SS Cake 7 | 9.96 | 22 | Off Cycle | 2.8 | 115 | 3 |  | 322 | 345 | 0 |  | Solenoid | SORITPI27
6 | [5 empty] | SPARE | [9 empty] | 0 |  | Solenoid | SORITPI27
7 | 8' | FT |  |  |  | Floral 9 | 8.5 | 30 | Off Cycle | 1.5 | 115 | 2 |  | 172.5 | 230 | 0 |  |  | SORITPI27
8 | 3 Door | NFD |  |  |  | Floral 10 | 5.7 | 30 | Off Cycle | 3 | 115 | 2 |  | 345 | 230 | 0 |  | Solenoid | SORITPI27
9 | 24' | P2E |  |  |  | Produce 19,20 | 23.28 | 24 | Off Cycle | 3 | 115 | 3 |  | 345 | 345 | 0 |  | Solenoid | SORITPI37
10 | 12' | PW/PWE |  |  |  | Produce Table 11-14 | 18.03 | 24 | Off Cycle | 2.64 | 115 |  |  | 303.6 | 0 | 0 |  |  | SORITPI27
11 | 12' | PW/PWE |  |  |  | Produce Table 15-18 | 18.03 | 24 | Off Cycle | 2.64 | 115 |  |  | 303.6 | 0 | 0 |  |  | SORITPI27
12 | 36' | P2E |  |  |  | Produce 21-24 | 34.9 | 24 | Off Cycle | 4.5 | 115 | 4.5 |  | 517.5 | 517.5 | 0 |  |  | SORITPI49
13 | 32' | D5LE |  |  |  | MD Produce 25-28 | 45.6 | 24 | Off Cycle | 7 | 115 | 5.1 |  | 805 | 586.5 | 0 |  | Solenoid | SORITPI49
14 | [5 empty] | SPARE | [7 empty] | 0 | 0 | 0 |  |  | SORITPI27
15 | 612 sq.ft | GAL66-270 |  | EXISTING |  | Produce Prep | 39.78 | 30 | Off Cycle | 9.6 | 115 |  |  | 1104 | 0 | 0 |  | Solenoid | SORITPI49
16 | 20x25 | HC6A-333 |  | EXISTING |  | Produce Cooler | 28 | 25 | Off Cycle | 12.6 | 115 |  |  | 1449 | 0 | 0 |  | Solenoid | SORITPI49
17 | 8x9 | HC4E-068 |  | EXISTING |  | Seafood Cooler | 6.4 | 20 | Off Cycle | 2.2 | 208 |  |  | 457.6 | 0 | 0 |  | Solenoid | SORITPI27
18 | 350 sq.ft | GAL46-180 |  | EXISTING |  | Seafood Prep | 40 | 30 | Off Cycle | 6.4 | 115 |  |  | 736 | 0 | 0 |  | Solenoid | SORITPI37
19 | [5 empty] | SPARE | [9 empty] | 0 |  | Solenoid | SORITPI27
20 | [5 empty] | SPARE | [7 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | EXISTING HP RACK B |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCXV6408
Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 16
Outside Air Temp. |  |  | 100 | 1 | 1 | 3DA3-075L-TFC | 75.6 | 20 | 7.5 |  | 41 |  | 3DA3R10ML-TFC |  |  | 0 | 60A | 50A | #6 | F P I |  | 8
Required Load Group 1 |  |  | 319.98 | 1 | 2 | 3DB3-100L-TFC | 90.3 | 20 | 10 |  | 43.6 |  | 3DB3R12ML-TFC |  |  | 0 | 60A | 50A | #6 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 450.4 | 1 | 3 | 3DS3-150L-TFC | 120 | 20 | 15 |  | 59.6 |  | 3DS3R17ML-TFC |  |  | 0 | 80A | 60A | #4 | FLA |  | 24
Effective capac. with subcooling |  |  | 450.4 | 1 | 4 | 4DA3-250L-TFC | 164.5 | 20 | 25 |  | 82.2 |  | 4DH3R22ML-TSK |  |  | 0 | 125A | 90A | #1 | MCA |  | 26
% Excess Capacity Group 1 |  |  | 28.96% | [16 empty] | MOPD |  | 30
Rej. Heat (MBH) Group 1 |  |  | 608.04 | [16 empty] | Weight |  | 2769
|  |  | 0 | [16 empty] | Size |  | 96 X 166
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 6
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2 1/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 1 5/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-9108 |  | Drain Regulator | [5 empty] | Air reclaim |  | 16D17B |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 608.04 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 304.02 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 37.5333 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs.

## Remodel Rack C
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack C | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy. |  |  |  | Location: | Beaufort, SC |  |  |  | Rack Model: | EXISTING HP RACK C | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2839 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/27/21 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
[11 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA | [6 empty] | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 600
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | ED-208/1 | Liquid | Suction | Run | Horiz | Riser | Horiz
[6 empty] | Loop LT 1 | [7 empty] | 0 | 0 | 0 |  | 1 3/8 | 2 5/8"
1 | 8X20 | HC6E-187 |  |  |  | Bakery Freezer | 15 | -15 | Electric |  |  |  |  | 0 | 0 | 0 |  | Solenoid | SORITPI411
2 | 12' | NF6 |  |  |  | Frozen Bakery 8 | 17.88 | -16 | Electric | 2.82 | 115 | 2.13 | 6.42 | 324.3 | 244.95 | 738.3 | 24.02 | Solenoid | SORITPI39
3 | 6' | LN |  |  |  | Seafood Promo 29 | 2.34 | -20 | Electric | 0.6 | 115 |  | 1.4 | 69 | 0 | 161 | 8 | Solenoid | SORITPI27
4 | 6' | LN |  |  |  | Seafood Promo 30 | 2.34 | -20 | Electric | 0.6 | 115 |  | 1.4 | 69 | 0 | 161 | 8 | Solenoid | SORITPI27
5 | 9 Drs | RL |  |  |  | Frozen Seafood 31,32 | 14 | -11 | Electric | 6.3 | 115 | 5.3 | 9.8 | 724.5 | 609.5 | 1127 | 40.8 | Solenoid | SORITPI37
6 | 8' | M1LGE |  |  |  | DT Seafood 33 | 4.24 | -20 | Electric | 0.48 | 115 |  | 0.75 | 55.2 | 0 | 86.25 | 6.6 | Solenoid | SORITPI27
7 | 8X9 | HC6E-117 |  | EXISTING |  | Seafood Freezer | 10 | -15 | Electric | 3.3 | 208 |  |  |  | 0 | 0 | 13.2 | Solenoid | SORITPI37
8 | [5 empty] | SPARE |  |  | none |  |  |  |  | 0 | 0 | 0 |  | Solenoid | SORITPI49
[6 empty] | LOOP LTB | [11 empty] | 1 1/8 | 3 5/8"
9 | 8' | LN |  |  |  | Meat Promo 42 | 3.12 | -20 | Electric | 0.6 | 115 |  | 1.4 | 69 | 0 | 161 | 8 | Solenoid | SORITPI27
10 | 8' | LN |  |  |  | Meat Promo 43 | 3.12 | -20 | Electric | 0.6 | 115 |  | 1.4 | 69 | 0 | 161 | 8 | Solenoid | SORITPI27
11 | 4 Drs | RL |  |  |  | Frozen Meat 47 | 6.24 | -11 | Electric | 2.8 | 115 | 2.42 | 4.36 | 322 | 278.3 | 501.4 | 18 | Solenoid | SORITPI27
12 | 17X30 | HC4E-210 |  | EXISTING |  | 1/2 Storage Freezer | 19.3 | -15 | Electric | 11 | 208 |  |  |  | 0 | 0 | 14.5 3/0 | Solenoid | SORITPI49
13 | 17X30 | HC4E-210 |  | EXISTING |  | 1/2 Storage Freezer | 19.3 | -15 | Electric | 11 | 208 |  |  |  | 0 | 0 | 14.5 3/0 | Solenoid | SORITPI49
14 | 14 Drs | RL |  |  |  | Frozen Food 83-85 | 21.8 | -11 | Electric | 9.8 | 115 | 8.2 | 15.26 | 1127 | 943 | 1754.9 | 63.6 | Solenoid | SORITPI49
15 | 17 Drs | RVZC |  |  |  | Frozen Food 72-75 | 15 | -7 | Electric | 4.8 | 115 | 10.18 | 15.92 | 552 | 1170.7 | 1830.8 | 68 | Solenoid | SORITPI411
16 | 17 Drs | RL |  |  |  | FF/Ice Cream 86-89 | 28.1 | -19 | Electric | 11.9 | 115 | 10.14 | 18.57 | 1368.5 | 1166.1 | 2135.55 | 76.6 | Solenoid | SORITPI411
17 | 18 Drs | RL |  |  |  | Ice Cream 79,90-92 | 29.7 | -19 | Electric | 12.6 | 115 | 10.67 | 19.62 | 1449 | 1227.05 | 2256.3 | 81.4 | Solenoid | SORITPI411
18 | 18 Drs | RVZC |  |  |  | Frozen Food 65,76-78 | 17.46 | -11 | Electric | 5.4 | 115 | 10.67 | 15.89 | 621 | 1227.05 | 1827.35 | 72 | Solenoid | SORITPI411
19 | 15 Drs | RL |  |  |  | Frozen Food 80-82 | 23.4 | -11 | Electric | 10.5 | 115 | 8.73 | 16.35 | 1207.5 | 1003.95 | 1880.25 | 68.4 | Solenoid | SORITPI411
20 | [5 empty] | SPARE
21 | [5 empty] | SPARE
22 | 14 Drs | RVZC |  |  |  | Frozen Food 69-71 | 13.16 | -16 | Electric | 4.2 | 115 | 8.2 | 13.06 | 483 | 943 | 1501.9 | 56 | Solenoid | SORITPI411
23 | 15 Drs | RVZC |  |  |  | Frozen Food 66-68 | 14.1 | -16 | Electric | 4.5 | 115 | 8.73 | 13.9 | 517.5 | 1003.95 | 1598.5 | 60 | Solenoid | SORITPI411
| General Specifications |  |  | Rack Model: |  | EXISTING HP RACK C |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R507 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCXV10408
Condensing Temp |  |  | 110 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 10.2
Outside Air Temp. |  |  | 100 | 1 | 1 | 4DL3-150E | 69.4 | -20 | 15 |  | 52.6 |  | 4DL3F63KL-TSK |  |  | 0 | 70A | 60A | #4 | F P I |  | 8
Required Load Group 1 |  |  | 279.6 | 1 | 2 | 4DL3-150E | 69.4 | -20 | 15 |  | 52.6 |  | 4DL3F63KL-TSK |  |  | 0 | 70A | 60A | #4 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 391.4 | 1 | 3 | 4DT3-220E | 84.2 | -20 | 22 |  | 66 |  | 4DT3F76KL-TSK |  |  | 0 | 90A | 75A | #3 | FLA |  | 40
Effective capac. with subcooling |  |  | 555.788 | 1 | 4 | 4DT3-220E | 84.2 | -20 | 22 |  | 66 |  | 4DT3F76KL-TSK |  |  | 0 | 90A | 75A | #3 | MCA |  | 42
% Excess Capacity Group 1 |  |  | 49.69% | 1 | 5 | 4DT3-220E | 84.2 | -20 | 22 |  | 66 |  | 4DT3F76KL-TSK |  |  | 0 | 90A | 75A | #3 | MOPD |  | 50
Rej. Heat (MBH) Group 1 |  |  | 637.982 | [16 empty] | Weight |  | 5350
|  |  | 0 | [16 empty] | Size |  | 96X274
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 10
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2 1/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2 1/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5202 |  | Drain Regulator | [5 empty] | Air reclaim |  | EXISTING |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 637.982 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 318.991 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 23.3 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs.
6