## Remodel Rack A
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy. |  |  |  | Location: | Beaufort, SC |  |  |  | Rack Model: | Existing HP Rack A | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2839 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | 712322 |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/27/21 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
APR | 11/5/21 | Kim Austin | Revised for remodel | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA | [6 empty] | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 600
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs |  | Liquid | Suction | Run | Horiz | Riser | Horiz
[6 empty] | Loop MT-1 | [7 empty] | 0 | 0 | 0 |  | 1 3/8 BV | 3 5/8 BV
1 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | Solenoid | SORITPI27
2 | 44'/28' | D5/DD5X |  |  |  | Beer Doors 60-63/N141-N143 | 30.4 | 30 | Off Cycle | 12 | 115 | 9.7 |  | 1380 | 1115.5 | 0 |  | Solenoid | SPT2 99
3 | [5 empty] | SPARE |  |  | Off Cycle | [8 empty] | Solenoid | SORITPI27
4 | 44' | DD5X |  |  |  | Dairy Doors N134-N137 | 13.2 | 30 | Off Cycle | 3.3 | 115 | 3.9 | 0 | 379.5 | 448.5 | 0 |  | Solenoid | SPT2 57 | 50 | 1 1/8 | 7/8 | 1/2
5 | 36' | DD5X |  |  |  | Dairy Doors N138-N140 | 10.8 | 30 | Off Cycle | 2.7 | 115 | 3.3 | 0 | 310.5 | 379.5 | 0 |  | Solenoid | SPT2 57 | 50 | 1 1/8 | 7/8 | 1/2
6 | 540 sq.ft. | HC8A-372BBALT |  | EXISTING |  | Dairy Cooler | 33.5 | 25 | Off Cycle | 12.6 | 115 |  |  | 1449 | 0 | 0 |  | Solenoid | SORITPI411
7 | 36' | DD5X |  |  |  | Dairy Doors N130-N133 | 10.8 | 30 | Off Cycle | 2.7 | 115 | 3.2 | 0 | 310.5 | 368 | 0 |  | Solenoid | SPT2 57
8 | 6' | M5X |  |  |  | MD Seafood N116 | 8.1 | 26 | Off Cycle | 0.9 | 115 | 0.9 | 0.65 | 103.5 | 103.5 | 74.75 |  | Solenoid | SPT2 57 | 50 | 7/8 | 7/8 | 1/2
9 | 52' | DD5X |  |  |  | Lunch Meat N124-N129 | 15.6 | 30 | Off Cycle | 3.9 | 115 | 4.6 | 0 | 448.5 | 529 | 0 |  | Solenoid | SPT2 79
10 | 32' | M5X |  |  |  | MD Meat N121-N123 | 44 | 26 | Off Cycle | 4.8 | 115 | 4.7 | 4.3 | 552 | 540.5 | 494.5 |  | Solenoid | SPT2 1111 | 50 | 1 1/8 | 1 1/8 | 1/2
11 | 19x28 | KRD56A-216 |  | NEW |  | 1/2 Meat Cooler (L) | 14.77 | 28 | Off Cycle | 4.5 | 115 |  |  | 915.2 | 0 | 0 |  | Solenoid | SPT2 99
12 | 19x28 | KRD56A-216 |  | NEW |  | 1/2 Meat Cooler (R) | 14.77 | 28 | Off Cycle | 4.5 | 115 |  |  | 915.2 | 0 | 0 |  | Solenoid | SPT2 99
13 | 28' | M5X |  |  |  | MD Meat N118-N120 | 38.5 | 26 | Off Cycle | 4.2 | 115 | 4.1 | 4.7 | 483 | 471.5 | 540.5 |  | Solenoid | SPT2 1111 | 50 | 1 1/8 | 1 1/8 | 1/2
14 | 600 sq.ft. | 2)GLD46A270 |  | NEW |  | Meat Prep | 39 | 30 | Off Cycle | 7.2 | 115 |  |  | 1104 | 0 | 0 |  | Solenoid | SPT2 1111
15 | [5 empty] | Subcool LT | 93.22 |  | none |  |  |  |  | 0 | 0 | 0 |  |  | ORIT 20
16 | [5 empty] | Future | [7 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing HP Rack A |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCXV8412
Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 11.49 | 15.2
Outside Air Temp. |  |  | 100 | 1 | 1 | 3DB3R12ME-TFC | 90.3 | 20 | 10 |  | 43.6 |  | 3DB3R12ML-TFC |  |  | 0 | 60A | 50A | #6 | F P I |  | 12
Required Load Group 1 |  |  | 366.66 | 1 | 2 | 3DF3A120L-TFC | 105 | 20 | 12 |  | 48.2 |  | 3DF3R15ML-TFC |  |  | 0 | 70A | 50A | #4 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 472.6 | 1 | 3 | 3DS3-150L | 107.5 | 20 | 15 |  | 59.6 |  | 3DS3R17ML-TFC |  |  | 0 | 80A | 60A | #4 | FLA |  | 32
Effective capac. with subcooling |  |  | 472.6 | 1 | 4 | 4DA3-200L | 127 | 20 | 20 |  | 66 |  | 4DA3R18ML-TSK |  |  | 0 | 90A | 75A | #3 | MCA |  | 35
% Excess Capacity Group 1 |  |  | 22.42% | NEW | 5 | 2DD3R63KL-TFC-441 | 42.8 | 20 | 5 |  | 22.3 |  |  |  |  | 0 | 30A | 30A | #10 | MOPD |  | 40
Rej. Heat (MBH) Group 1 |  |  | 638.01 | [16 empty] | Weight |  | 2880
|  |  | 0 |  |  | CHANGE 4DK3R22ME-TSK TO 2DD3R63KL | [13 empty] | Size |  | 96x220
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 8 | 6
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)1 5/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2) 1 3/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-9108 |  | Drain Regulator | [5 empty] | Air reclaim |  | 16D17B |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 16D17B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  | PUMP OUT KIT |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 638.01 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 319.005 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 39.3833 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs.

## Remodel Rack B
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy. |  |  |  | Location: | Beaufort, SC |  |  |  | Rack Model: | EXISTING HP RACK B | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2839 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | 712322 |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/27/21 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
APR | 11/5/21 | Kim Austin | Revised for remodel | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA | [6 empty] | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 400
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
[6 empty] | Loop MT-2 | [7 empty] | 0 | 0 | 0 |  | 1 3/8 | 3 1/8 & 2 5/8
1 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | Solenoid | SORITPI27
2 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | Solenoid | SORITPI27
3 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | Solenoid | SORITPI27
4 | 6'6'12'10' | Q3/Q4/Q4/Q4 |  |  |  | SS Deli N93-N96 | 37.4 | 22 | Off Cycle | 3 | 115 | 4.2 |  | 345 | 483 | 0 |  | Solenoid | SPT2 1111 | 50 | 1 11/8 | 1 1/8 | 1/2
5 | 16'6'4'12'8' | Q4/VR3HV/VR3HV/S6S/D5X |  |  |  | Deli/Bakery N97-N102 | 55.1 | 22 | Off Cycle | 5.4 | 115 | 5.6 | 0 | 621 | 644 | 0 |  | Solenoid | SPT 1313 | 50 | 1 3/8 | 1 3/8 | 5/8
6 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | Solenoid | SORITPI27
7 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  |  | SORITPI27
8 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | Solenoid | SORITPI27
9 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | Solenoid | SORITPI37
10 | 16' | DD5X |  |  |  | Produce Doors N112,N113 | 4.8 | 30 | Off Cycle | 1.2 | 115 | 1.4 | 0 | 138 | 161 | 0 |  |  | SPT2 37 | 50 | 7/8 | 7/8 | 1/2
11 | [5 empty] | SPARE |  |  | Off Cycle | [5 empty] | 0 | 0 |  |  | SORITPI27
12 | 24' | D5X |  |  |  | Produce N109-N111 | 32.4 | 24 | Off Cycle | 1.8 | 115 | 1.8 | 0 | 207 | 207 | 0 |  |  | SPT2 911
13 | 48' | D5X |  |  |  | MD Produce N105-N108 | 64.8 | 24 | Off Cycle | 3.6 | 115 | 4.3 | 0 | 414 | 494.5 | 0 |  | Solenoid | SPT 1313
14 | [5 empty] | SPARE | [7 empty] | 0 | 0 | 0 |  |  | SORITPI27
15 | 612 sq.ft | GAL66-270 |  | EXISTING |  | Produce Prep | 39.78 | 30 | Off Cycle | 9.6 | 115 |  |  | 1104 | 0 | 0 |  | Solenoid | SORITPI49
16 | 20x25 | KRD66A340 |  | NEW |  | Produce Cooler | 28 | 25 | Off Cycle | 12.6 | 115 |  |  | 1449 | 0 | 0 |  | Solenoid | SPT2 911
17 | 8x9 | KRD26A-125 |  | NEW |  | Seafood Cooler | 6.4 | 28 | Off Cycle | 1.8 | 115 |  |  | 457.6 | 0 | 0 |  | Solenoid | SPT2 57
18 | 350 sq.ft | GLD56A340 |  | NEW |  | Seafood Prep | 40 | 30 | Off Cycle | 4.5 | 115 |  |  | 736 | 0 | 0 |  | Solenoid | SPT2 1111
19 | [5 empty] | SPARE | [9 empty] | 0 |  | Solenoid | SORITPI27
20 | [5 empty] | SPARE | [7 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | EXISTING HP RACK B |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCXV6408
Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 14.1
Outside Air Temp. |  |  | 100 | 1 | 1 | 3DA3-075L-TFC | 75.6 | 20 | 7.5 |  | 41 |  | 3DA3R10ML-TFC |  |  | 0 | 60A | 50A | #6 | F P I |  | 8
Required Load Group 1 |  |  | 308.68 | NEW | 2 | 2DC3R53KL-TFC-441 | 36.6 | 20 | 5 |  | 22.3 |  |  |  |  | 0 | 30A | 30A | #10 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 396.7 | 1 | 3 | 3DS3-150L-TFC | 120 | 20 | 15 |  | 59.6 |  | 3DS3R17ML-TFC |  |  | 0 | 80A | 60A | #4 | FLA |  | 24
Effective capac. with subcooling |  |  | 396.7 | 1 | 4 | 4DA3-250L-TFC | 164.5 | 20 | 25 |  | 82.2 |  | 4DH3R22ML-TSK |  |  | 0 | 125A | 90A | #1 | MCA |  | 26
% Excess Capacity Group 1 |  |  | 22.19% | [16 empty] | MOPD |  | 30
Rej. Heat (MBH) Group 1 |  |  | 535.545 |  |  | CHANGE 3DB3-100L-TFC TO 2DC3R53KL-TFC-441 | [13 empty] | Weight |  | 2769
|  |  | 0 | [16 empty] | Size |  | 96 X 166
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 6
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)1 5/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 3/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-9108 |  | Drain Regulator | [5 empty] | Air reclaim |  | 16D17B |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 16D17B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  | PUMP OUT KIT |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 535.545 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 267.7725 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 33.0583 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs.

## Remodel Rack C
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack C | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy. |  |  |  | Location: | Beaufort, SC |  |  |  | Rack Model: | EXISTING HP RACK C | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2839 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | 712322 |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/27/21 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
APR | 11/5/21 | Kim Austin | Revised for remodel | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA | [6 empty] | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 600
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | ED-208/1 | Liquid | Suction | Run | Horiz | Riser | Horiz
[6 empty] | Loop LT 1 | [7 empty] | 0 | 0 | 0 |  | 1 3/8 | 2 5/8"
1 | 8X20 | HC6E-187 |  |  |  | Bakery Freezer | 15 | -15 | Electric |  |  |  |  | 0 | 0 | 0 |  | Solenoid | SORITPI411
2 | 6 Drs | RL |  |  |  | Frozen Bakery N103,N104 | 6.4 | -19 | Electric | 1.8 | 115 | 1 | 4.6 | 207 | 115 | 529 | 20.1 | Solenoid | SPT2 79
3 | 16' | FN |  |  |  | Seafood Promo N114,N115 | 6 | -18 | Electric | 0.4 | 115 | 0 | 1.4 | 46 | 0 | 161 | 15.4 | Solenoid | SPT2 79
4 | [8 empty] | Electric | [8 empty] | Solenoid
5 | 5 Drs | RL |  |  |  | Frozen Seafood 31 | 7.8 | -11 | Electric | 3.5 | 115 | 2.91 | 5.45 | 402.5 | 334.65 | 626.75 | 22.8 | Solenoid | SPT2 79
6 | 8' | GMD 8RG |  |  |  | Service Seafood N117 | 5.2 | 15 | Off Cycle | 0.48 | 115 | 0.72 |  | 55.2 | 82.8 |  |  | Solenoid | SPT2 37
7 | 8X9 | HC6E-117 |  | EXISTING |  | Seafood Freezer | 10 | -15 | Electric | 3.3 | 208 |  |  |  | 0 | 0 | 13.2 | Solenoid
8 | [5 empty] | SPARE |  |  | none |  |  |  |  | 0 | 0 | 0 |  | Solenoid
[6 empty] | LOOP LTB | [11 empty] | 1 1/8 | 3 5/8"
9 | 8' | FN |  |  |  | Meat Promo N126 | 3 | -18 | Electric | 0.24 | 115 | 0 | 0.67 | 27.6 | 0 | 77.05 | 7.7 | Solenoid | SPT2 37
10 | [8 empty] | Electric | [8 empty] | Solenoid
11 | 4 Drs | RL |  |  |  | Frozen Meat 47 | 6.24 | -11 | Electric | 2.8 | 115 | 2.42 | 4.36 | 322 | 278.3 | 501.4 | 18 | Solenoid | SORITPI27
12 | 17X30 | MKD34E315 |  | NEW |  | 1/2 Storage/IC Freezer | 19.3 | -18 | Electric | 7.8 | 230/1 |  |  |  | 0 | 0 | 21.5 3PH | Solenoid | SPT2 1111
13 | 17X30 | MKD34E315 |  | NEW |  | 1/2 Storage/IC Freezer | 19.3 | -18 | Electric | 7.8 | 230/1 |  |  |  | 0 | 0 | 21.5 3PH | Solenoid | SPT2 1111
14 | 14 Drs | RL |  |  |  | Frozen Food 83-85 | 21.8 | -11 | Electric | 9.8 | 115 | 8.2 | 15.26 | 1127 | 943 | 1754.9 | 63.6 | Solenoid | SORITPI49
15 | 17 Drs | RVZC |  |  |  | Frozen Food 72-75 | 15 | -7 | Electric | 4.8 | 115 | 10.18 | 15.92 | 552 | 1170.7 | 1830.8 | 68 | Solenoid | SORITPI411
16 | 17 Drs | RL |  |  |  | FF/Ice Cream 86-89 | 28.1 | -19 | Electric | 11.9 | 115 | 10.14 | 18.57 | 1368.5 | 1166.1 | 2135.55 | 76.6 | Solenoid | SORITPI411
17 | 18 Drs | RL |  |  |  | Ice Cream 79,90-92 | 29.7 | -19 | Electric | 12.6 | 115 | 10.67 | 19.62 | 1449 | 1227.05 | 2256.3 | 81.4 | Solenoid | SORITPI411
18 | 18 Drs | RVZC |  |  |  | Frozen Food 65,76-78 | 17.46 | -11 | Electric | 5.4 | 115 | 10.67 | 15.89 | 621 | 1227.05 | 1827.35 | 72 | Solenoid | SORITPI411
19 | 15 Drs | RL |  |  |  | Frozen Food 80-82 | 23.4 | -11 | Electric | 10.5 | 115 | 8.73 | 16.35 | 1207.5 | 1003.95 | 1880.25 | 68.4 | Solenoid | SORITPI411
20 | [5 empty] | SPARE
21 | [5 empty] | SPARE
22 | 14 Drs | RVZC |  |  |  | Frozen Food 69-71 | 13.16 | -16 | Electric | 4.2 | 115 | 8.2 | 13.06 | 483 | 943 | 1501.9 | 56 | Solenoid | SORITPI411
23 | 15 Drs | RVZC |  |  |  | Frozen Food 66-68 | 14.1 | -16 | Electric | 4.5 | 115 | 8.73 | 13.9 | 517.5 | 1003.95 | 1598.5 | 60 | Solenoid | SORITPI411
| General Specifications |  |  | Rack Model: |  | EXISTING HP RACK C |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R507 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCXV10408
Condensing Temp |  |  | 110 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 7.93
Outside Air Temp. |  |  | 100 | NEW | 1 | 2DL3F20KL-TFC-441 | 22.4 | -20 | 15 |  | 26.3 |  | 4DL3F63KL-TSK |  |  | 0 | 40A | 30A | #8 | F P I |  | 8
Required Load Group 1 |  |  | 260.96 | 1 | 2 | 4DL3-150E | 69.4 | -20 | 15 |  | 52.6 |  | 4DL3F63KL-TSK |  |  | 0 | 70A | 60A | #4 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 305.6 | NEW | 3 | 3DF3F40KL-TFC-441 | 45.4 | -20 | 22 |  | 39 |  | 4DT3F76KL-TSK |  |  | 0 | 50A | 40A | #6 | FLA |  | 40
Effective capac. with subcooling |  |  | 433.952 | 1 | 4 | 4DT3-220E | 84.2 | -20 | 22 |  | 66 |  | 4DT3F76KL-TSK |  |  | 0 | 90A | 75A | #3 | MCA |  | 42
% Excess Capacity Group 1 |  |  | 39.86% | 1 | 5 | 4DT3-220E | 84.2 | -20 | 22 |  | 66 |  | 4DT3F76KL-TSK |  |  | 0 | 90A | 75A | #3 | MOPD |  | 50
Rej. Heat (MBH) Group 1 |  |  | 498.128 | [16 empty] | Weight |  | 5350
|  |  | 0 |  |  | CHANGE 4DL3-150E TO 2DL3F20KL-TFC-441 | [13 empty] | Size |  | 96X274
Required Load Group 2 |  |  | 0 |  |  | CHANGE 4DT3-220E TO 3DF3F40KL-TFC-441 | [13 empty] | # of Fans |  | 10
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)1 3/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 1/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5202 |  | Drain Regulator | [5 empty] | Air reclaim |  | 12D13B |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8 | 1 5/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8 | 1 5/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 12D13B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  | PUMP OUT KIT |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 498.128 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 249.064 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 21.7467 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs.
6