## Master Revisions
2009-05-13 | Added Bohn condenser model to condenser look, increased table range
2010-09-30 | Change circuit lookup from 3 manufacturers to 1 for CIRLOOK for all 3 manufacturers
2011-04-04 | Add 4DH3S16ML compressor, change 90A breaker requirement in lookup down to 65.5A.
2011-06-30 | Add KW Stratus cases. Starts with 2012 Grand opening stores, CIRLOOK to 4000 lines
2011-06-30 | Add KW Stratus cases. Starts with 2012 Grand opening stores, CIRLOOK to 4000 lines
2011-06-30 | Update LT to no Oil cooler models, 4DH, 4DJ
2014-03-13 | Add RDD & RDS condensers
2014-03-14 | Update cirlook
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07
2026-07-29 06:07

## Rack Nomenclature
Legend Sheet Program
Release 8.0
I n s t r u c t i o n s :
Rack | Rack | MBTUH |  |  |  |  | Pages
No | Nomenclature | Totals | Enter the rack nomenclature exactly as you want it |  | Memory | Name | Included
1 | Rack A |  | to appear. Your entry must fit the space provided. |  | #N/A | Rack A | 1
2 | Rack A | Total | If two or more pages (racks) have the same name, |  | #N/A | Rack A | 1
3 | Rack B | Total | the total MBTUH loads will be displayed on the last |  |  | Rack B | 1
4 | Rack A +15 | Total | page of the group. The "MBTUH Totals" column |  | #N/A | Rack A +15 | 1
5 | Rack B +20 | Total | identifies which racks will display the totaled MBTUH |  | #N/A | Rack B +20 | 1
6 | Rack C | Total | values. |  |  | Rack C | 1
7 | Rack D | Total |  |  |  | Rack D | 1
8 |  |  |  |  | FALSE | None | 0
Available Memory
| #N/A | Bytes | #N/A | %

## Rack A Part 1
1 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Display Systems | 1
0 | 2016 Gees Mill Road |  |  |  | Location: | Kings Mountain, NC. |  |  |  | Rack Model: | EXISTING HP | [12 empty] | 1925 Ruffin Mill Road
1 | Conyers, Georgia 30013 |  |  |  | Store #: | 2654 | MED |  |  | Salesman | [13 empty] | Colonial Heights, VA 23834 | 1
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: | 92617 |  |  |  | Prepared By: | SYON |  | Date Originated |  |  | 7/30/2007 | [7 empty] | (804) 526-4455, Fax: (804) 526-1926
1 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC |  | 1
[12 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
1 | [11 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
[12 empty] | MCA | [6 empty] | Fixture Plan:
1 | [11 empty] | Max. Overcurrent | [12 empty] | 1
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
1 | Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 1 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 1Sat | 1Sat2
| 1 | 89 Sq. Ft. | AA28-106B |  |  | 1 | Deli/Bakery Cooler | 7.4 | 27 | OC | 4 | 120 |  |  | 480 | 0 | 0 |  |  | SORIT-12 | 190 | 7/8" | 7/8" | 5/8" |  | 0 | 0
| 2 | 8'4'12'8'6' | PT67/PT67/BDPF/PTD54RRS/PT72 |  |  | 1 | Deli Lineup 28-32 | 40 | 24 | OC | 6.5 | 120 | 10 | 0.4 | 780 | 1200 | 48 |  |  | SORIT-20 | 220 | 1-5/8" | 1-3/8" | 7/8" |  | 0 | 0
| 3 | 12'12'12' | O5DM-E |  |  | 1 | Dairy 24-26 | 52.9 | 26 | OC | 6 | 120 | 2.4 |  | 720 | 288 | 0 |  |  | SORIT-20 | 130 | 1-5/8" | 1-3/8" | 7/8" |  | 0 | 0
| 4 | 8'12'12'12'6' | O5DM-E |  |  | 1 | Dairy 19-23 | 71.5 | 26 | OC | 8 | 120 | 3.4 |  | 960 | 408 | 0 |  |  | SORIT-20 | 100 | 1-5/8" | 1-3/8" | 7/8" |  | 0 | 0
| 5 | 8'8'12'12' | O5DM-E |  |  | 1 | Beer 37-40 | 58.8 | 26 | OC | 7 | 120 | 2.8 |  | 840 | 336 | 0 |  |  | SORIT-20 | 100 | 1-5/8" | 1-3/8" | 5/8" |  | 0 | 0
| 6 | 20x12x8 | AA38-160B |  |  | 1 | Dairy Cooler | 14.1 | 25 | OC | 6 | 120 |  |  | 720 | 0 | 0 |  |  | SORIT-12 | 60 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 7 | 30x20x10 | 2) FL36-135 |  |  | 1 | Meat Prep | 33 | 30 | OC | 6.6 | 120 |  |  | 792 | 0 | 0 |  |  | SORIT-20 | 60 | 1-3/8" | 1-1/8" | 5/8" |  | 0 | 0
| 8 | 16x20x8 | AA46-192B |  |  | 1 | Meat Cooler | 16.5 | 25 | OC | 8 | 120 |  |  | 960 | 0 | 0 |  |  | SORIT-12 | 80 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 9 | 12x20x8 | AA38-160B |  |  | 1 | Produce Cooler | 14.1 | 29 | OC | 6 | 120 |  |  | 720 | 0 | 0 |  |  | SORIT-12 | 90 | 7/8" | 7/8" | 5/8" |  | 0 | 0 | 464.932
| 10 | 480 Sq. Ft. | FL36-135A |  |  | 1 | Prod Prep | 26.7 | 30 | OC | 3.3 | 120 |  |  | 396 | 0 | 0 |  | ME14S250 | SORIT-15 | 100 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0 | 0
| 11 | 8'12'12' | O5DM-E |  |  | 1 | Lunch Meat 14-16 | 50.2 | 22 | OC | 5.5 | 120 | 2.2 |  | 660 | 264 | 0 |  |  | SORIT-20 | 50 | 1-5/8" | 1-3/8" | 5/8" |  | 0 | 0 | 0
| 12 | 8'12'12'12'12 | 56' DX6LD |  |  | 1 | MD Fresh Meat 13 | 16.632 | 28 | OC | 1.8 | 115 | 8.72 | 8.5 | 207 | 1002.8 | 977.5 | 0 | 0 | SORIT-12 | 70 | 7/8" | 7/8" | 5/8" | 8OHMH | 0 | 0 | 464.932
| 13 | 8'12' | OHMH-E |  |  | 1 | MD Fresh Meat 11,12 | 28.7 | 22 | OC | 4.5 | 120 | 1.4 | 1.4 | 540 | 168 | 168 |  |  | SORIT-20 | 100 | 1-3/8" | 1-1/8" | 5/8" |  | 0 | 0
| 14 | 12'12' | OHMH-E |  |  | 1 | MD Fresh Meat 9,10 | 34.4 | 22 | OC | 5 | 120 | 1.6 | 1.6 | 600 | 192 | 192 |  |  | SORIT-20 | 100 | 1-3/8" | 1-1/8" | 5/8" |  | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  | EXISTING HP |  |  | Compressor Specifications | [11 empty] | Condenser
1 | Refrigerant Type |  |  |  | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  |  |  | 1 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  |  | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. | [5 empty] | COMP1SAT | COMP1SAT2
1 | Outside Air Temp. | [19 empty] | F P I |  |  |  | 1 |  | 0 | 0
| Required Load Group 1 |  |  | 0 | [16 empty] | Voltage | [5 empty] | 0 | 0
1 | Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA |  |  |  | 1 |  | 0 | 0
| Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA | [5 empty] | 0 | 0 | 0 | MBTUH_COMP1
1 | % Excess Capacity Group 1 | [19 empty] | MOPD |  |  |  | 1 |  | 0 | 0 | 0 | MBTUH_COMP1SAT
| Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight | [5 empty] | 0 | 0 | 0 | MBTUH_COMP1SAT2
1 |  |  |  | 0 | [16 empty] | Size |  |  |  | 1 |  | 0 | 0 | 0 | MBTUH_COMP1MAIN
0 | Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans | [5 empty] | 0 | 0
1 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  |  |  | 1 |  | 0 | 0
| Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From | [5 empty] | 0 | 0
1 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 1
0 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT |  |  |  |  | 1
1 |  |  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
0 | Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To | [8 empty] | 1
1 | Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
| Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed |  |  |  |  | 1
1 | % Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve |  |  |  |  | 1
1 |  |  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
| Total Rej. Heat (MBH) |  |  | 0 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid |  |  |  |  | 1
1 | Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
| Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To |  |  |  |  | 1
1 | Rack Size
| Estimated Rack Weight Lbs. | [23 empty] | 1
1
1

## Rack A Part 2
2 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Display Systems | 2
| 2016 Gees Mill Road |  |  |  | Location: | Kings Mountain, NC. |  |  |  | Rack Model: | EXISTING HP | [12 empty] | 1925 Ruffin Mill Road
2 | Conyers, Georgia 30013 |  |  |  | Store #: | 2654 | MED |  |  | Salesman | [13 empty] | Colonial Heights, VA 23834 | 2
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: | 92617 |  |  |  | Prepared By: | SYON |  | Date Originated |  |  | 7/30/2007 | [7 empty] | (804) 526-4455, Fax: (804) 526-1926
2 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC |  | 2
[12 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
2 | [11 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
[12 empty] | MCA |  |  |  | 360.15 |  |  | Fixture Plan:
2 | [11 empty] | Max. Overcurrent |  |  |  | 400 | [8 empty] | 2
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
2 | Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 2 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 2Sat | 2Sat2
| 15 | 12'12' | O5DM-E | Retrofit Doors |  | 1 | MD Produce 7,8 | 23.6 | 22 | OC | 4 | 120 | 1.6 |  | 480 | 192 | 0 |  | *ME6S140 | SORIT-20 | 200 | 1-5/8" | 1-3/8" | 7/8" |  | 0 | 0
| 16 | 8'12'4' | 24' OHP-E |  |  | 1 | MD Produce 4-6 | 20.52 | 28 | OC | 2.1 | 115 | 1.4 | 0.61 | 241.5 | 161 | 70.15 | 0 | 0 | SORIT-20 | 240 | 1-3/8" | 1-1/8" | 5/8" | 8'12OHP | 0 | 0
| 17 | 8'12'/4' | O5DM-E/FT |  |  | 1 | MD Produce/Floral 1-3 | 33.2 | 26 | OC | 3.8 | 120 | 1.6 |  | 456 | 192 | 0 |  |  | SORIT-20 | 230 | 1-3/8" | 7/8" | 5/8" |  | 0 | 0
| 18 | [5 empty] | Spare |  |  | OC |  |  |  |  | #VALUE! | #VALUE! | #VALUE! |  | Ball Valve | Ball Valve | [5 empty] | 0 | 0
| 19 | [5 empty] | Spare | 0 |  | OC |  |  |  |  | #VALUE! | #VALUE! | #VALUE! |  | Ball Valve | Ball Valve | [5 empty] | 0 | 0
| 20 | [5 empty] | Subcool Low Temp | 44.1 | 40 | NA |  |  |  |  | #VALUE! | #VALUE! | #VALUE! |  |  | ORIT-20 | 150 | 1-3/8" |  |  |  | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 121.42
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 121.42
[15 empty] | #VALUE! | #VALUE! | #VALUE! |  | *LLSV & T'stat at door case | [6 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  | EXISTING HP |  |  | Compressor Specifications | [11 empty] | Condenser
2 | Refrigerant Type |  |  | R407A | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | ACE 147FB |  | 2 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 11.2269 |  |  |  | COMP2SAT | COMP2SAT2
2 | Outside Air Temp. |  |  | 100 |  | 1 | 2DA3R89KL-TFC | 59.79 | 20 | 7.5 |  | 32 |  | 2DA3R89KL-TFC |  |  | 0 | 40A | 40A | #8 | F P I |  | 10 |  | 2 |  | 0 | 0
| Required Load Group 1 |  |  | 586.352 |  | 2 | 2DA3R89KL-TFC | 59.79 | 20 | 7.5 |  | 32 |  | 2DA3R89KL-TFC |  |  | 0 | 40A | 40A | #8 | Voltage |  | 208/60/3 |  |  |  | 0 | 0
2 | Comp. Capacity Group 1 |  |  | 651 |  | 3 | 3DB3R12ML-TFC | 87.5 | 20 | 10 |  | 43.6 |  | 3DB3R12ML-TFC |  |  | 0 | 60A | 50A | #6 | FLA |  | 39.2 |  | 2 |  | 0 | 0
1 | Effective capac. with subcooling |  |  | 651 |  | 4 | 3DS3R17ML-TFC | 116.12 | 20 | 15 |  | 59.6 |  | 3DS3R17ML-TFC |  |  | 0 | 80A | 60A | #4 | MCA |  | 39.9 |  |  |  | 0 | 0 | 651 | MBTUH_COMP2
2 | % Excess Capacity Group 1 |  |  | 11.03% |  | 5 | 4DH3R22ML-TSK | 163.9 | 20 | 25 |  | 82.2 |  | 4DH3R22ML-TSK |  |  | 0 | 125A | 90A | #1 | MOPD |  | 40 |  | 2 |  | 0 | 0 | 0 | MBTUH_COMP2SAT
1.39 | Rej. Heat (MBH) Group 1 |  |  | 904.89 |  | 6 | 4DH3R22ML-TSK | 163.9 | 20 | 25 |  | 82.2 |  | 4DH3R22ML-TSK |  |  | 0 | 125A | 90A | #1 | Weight |  | 4771 |  |  |  | 0 | 0 | 0 | MBTUH_COMP2SAT2
2 |  |  |  | 0 | [16 empty] | Size |  | 96"x338" |  | 2 |  | 0 | 0 | 651 | MBTUH_COMP2MAIN
0 | Required Load Group 2 |  |  | 0 |  |  |  |  | 0 | [11 empty] | # of Fans |  | 2x7 |  |  |  | 0 | 0
2 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2) 2 1/8 |  | 2 |  | 0 | 0
| Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2) 2 1/8 |  |  |  | 0 | 0
2 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 2
0 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5203 |  | Drain Regulator | [5 empty] | Air reclaim |  | 16D17B |  | Head Fan LT/MT |  | NO
2 |  |  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  | NO |  |  | 2
0 | Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  | 2 1/8 |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
2 | Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8 | [6 empty] | 2
| Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
2 | % Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 16D17B-SC |  |  |  | 1 | 2 | 3 | 2
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
2 |  |  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  | H |  | Check Valve |  |  |  |  | 2
| Total Rej. Heat (MBH) |  |  | 904.89 |  | Suction Filter -- Group 1 |  | 2) BTAS525 |  | Subcooler | [5 empty] | Dia. x Length |  | 14x120 |  | Solenoid
2 | Heat Reclaim Avail. (MBH) |  |  | 452.445 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R |  |  |  |  | 2
| Compressor Capacity (Tons) |  |  | 54.3 |  | Drier |  | C19217 |  | TEV | [9 empty] | From / To
2 | Rack Size | [23 empty] | 2
Estimated Rack Weight Lbs.
2 | [24 empty] | 2

## Rack B
3 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | [13 empty] | Display Systems | 3
| 2016 Gees Mill Road |  |  |  | Location: | Kings Mountain, NC. |  |  |  | Rack Model: | EXISTING HP | [12 empty] | 1925 Ruffin Mill Road
3 | Conyers, Georgia 30013 |  |  |  | Store #: | 2654 | MED |  |  | Salesman | [13 empty] | Colonial Heights, VA 23834 | 3
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: | 92617 |  |  |  | Prepared By: | SYON |  | Date Originated |  |  | 7/30/2007 | [7 empty] | (804) 526-4455, Fax: (804) 526-1926
3 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC |  | 3
[12 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
3 | [11 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
[12 empty] | MCA |  |  |  | #N/A |  |  | Fixture Plan:
3 | [11 empty] | Max. Overcurrent |  |  |  | #N/A | [8 empty] | 3
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
3 | Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 3 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 3Sat | 3Sat2
| 1 | 20x13x8 | AG54-180B |  |  | 1 | Storage Freezer | 16.3 | -18 | HG 2 Wire | 5 | 208 |  |  | 1040 | 0 | 0 | E14S250 | ME14S250 | SORIT-15 | 70 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 2 | 10x16x8 | ITG34-390 |  |  | 1 | Ice Cream Freezer | 12.9 | -18 | HG 2 Wire | 9.6 | 208 |  |  | 1996.8 | 0 | 0 | E14S250 | ME14S250 | SORIT-12 | 100 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 3 | 5,2 | ORZ-E ELM |  |  | 1 | Frozen Meat/Seafood 17,18 | 9.4 | -12 | HG 2 Wire | 3.6 | 120 | 4.4 | 7.3 | 432 | 528 | 876 | E14S250 |  | SORIT-12 | 120 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 4 | 5,4 | ORZ-E ELM/ORZ |  |  | 1 | Frozen Food 49,50 | 10 | -12 | HG 4 Wire | 4.4 | 120 | 3.5 | 12.8 | 528 | 420 | 1536 | E14S250 |  | SORIT-15 | 130 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 5 | 5,3 | ORZ-E ELM/ORZ |  |  | 1 | Frozen Food 47,48 | 9 | -12 | HG 4 Wire | 4 | 120 | 3.4 | 11.8 | 480 | 408 | 1416 | E14S250 |  | SORIT-12 | 110 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 6 | 5,5, | ORZ-E ELM |  |  | 1 | Frozen Food 54,55 | 11.9 | -12 | HG 4 Wire | 5 | 120 | 5.8 | 17.2 | 600 | 696 | 3312 | E14S250 |  | SORIT-12 | 115 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 7 | 5,5,5 | ORZ-E ELM |  |  | 1 | Frozen Food 51-53 | 17.865 | -12 | HG 2 Wire | 7.5 | 120 | 8.7 | 25.8 | 900 | 1044 | 3096 | E14S250 |  | SORIT-15 | 160 | 1-3/8" | 1-1/8" | 5/8" |  | 0 | 0
| 8 | 10x8x8 | AG26-92B |  |  | 1 | Deli/Bakery Fzr | 8.5 | -15 | HG 2 Wire | 2 | 208 |  |  | 416 | 0 | 0 | E14S250 | ME14S250 | SORIT-12 | 200 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
| 9 | 3,3,5,5 | ORZ-E ELM |  |  | 1 | Ice Cream 33-36 | 19.7 | -17 | HG 2 Wire | 8 | 120 | 9.6 | 27.8 | 960 | 1152 | 3336 | E14S250 |  | SORIT-15 | 140 | 1-3/8" | 1-1/8" | 5/8" |  | 0 | 0 | 148.343 | MBTUH_3
| 10 | 2,2,2 | #N/A |  |  | #N/A | Frozen Ends 41,46,56 | 7.35 | #N/A | #N/A | 3 | #N/A | 4.5 | 11.4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 125 | 1 1/8 | 7/8" | 5/8" | 3,3ORZIC | 0 | 0 | 0 | MBTUH_3Sat
| 11 | 3 | ORZ-E |  |  | 1 | Frozen Bakery 27 | 4 | -11 | HG 2 Wire | 1.5 | 120 | 1.9 | 4.9 | 180 | 228 | 588 | E14S250 |  | SORIT-12 | 200 | 7/8" | 7/8" | 5/8" |  | 0 | 0 | 0 | MBTUH_3Sat2
| 12 | 5,4 | ORZ-E ELM |  |  | 1 | Frozen Food 42,43 | 9.528 | -12 | HG 4 Wire | 4 | 120 | 4.8 | 13.8 | 480 | 576 | 1656 | E14S250 |  | SORIT-12 | 130 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0 | 148.343 | MBTUH_3Main
| 13 | 5,5 | ORZ-E ELM |  |  | 1 | Frozen Food 44,45 | 11.9 | -12 | HG 4 Wire | 5 | 120 | 5.8 | 17.2 | 600 | 696 | 2064 | E14S250 |  | SORIT-12 | 110 | 1-1/8" | 7/8" | 5/8" |  | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  | EXISTING HP |  |  | Compressor Specifications | [11 empty] | Condenser
3 | Refrigerant Type |  |  | R507 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | ACE 038FB |  | 3 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  | 110 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | #N/A |  |  |  | COMP3SAT | COMP3SAT2
3 | Outside Air Temp. |  |  | 100 |  | 1 | 2DL3F20KL-TFC | 22.4 | -20 | 7.5 |  | 31.6 |  | 2DL3R78KL-TFC |  |  | 0 | 40A | 40A | #8 | F P I |  | #N/A |  | 3 |  | 0 | 0
| Required Load Group 1 |  |  | 148.343 |  | 2 | 3DB3F33KL-TFC | 37.2 | -20 | 10 |  | 43.6 |  | 3DB3R12ML-TFC |  |  | 0 | 60A | 50A | #6 | Voltage |  | #N/A |  |  |  | 0 | 0
3 | Comp. Capacity Group 1 |  |  | 111.3 |  | 3 | 3DS3F46KL-TFC | 51.7 | -20 | 15 |  | 59.6 |  | 3DS3R17ML-TFC |  |  | 0 | 80A | 60A | #4 | FLA |  | #N/A |  | 3 |  | 0 | 0
1.42 | Effective capac. with subcooling |  |  | 158.046 | [16 empty] | MCA |  | #N/A |  |  |  | 0 | 0 |  | 111.3 | MBTUH_COMP3
3 | % Excess Capacity Group 1 |  |  | 6.541% | [16 empty] | MOPD |  | #N/A |  | 3 |  | 0 | 0 |  | 0 | MBTUH_COMP3SAT
1.63 | Rej. Heat (MBH) Group 1 |  |  | 181.419 | [16 empty] | Weight |  | #N/A |  |  |  | 0 | 0 |  | 0 | MBTUH_COMP3SAT2
3 |  |  |  | 0 | [16 empty] | Size |  | #N/A |  | 3 |  | 0 | 0 |  | 111.3 | MBTUH_COMP3MAIN
0 | Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | #N/A |  |  |  | 0 | 0
3 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2) 1 1/8 |  | 3 |  | 0 | 0
1.24 | Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2) 7/8 |  |  |  | 0 | 0
3 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 3
1.64 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5290 |  | Drain Regulator | [5 empty] | Air reclaim |  | 8D9B |  | Head Fan LT/MT |  | YES |  |  | 0
3 |  |  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  | 8D9B |  | Crankcase Htrs. |  |  |  |  | 3
0 | Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  | 1 3/8 |  | Surge Solenoid | [5 empty] | Line size To |  | 1 1/8
3 | Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 1 1/8 | [6 empty] | 3
| Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  | A81BL1 3/8 |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
3 | % Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 8D9B-SC |  |  |  | 1 | 2 | 3 | 3
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
3 |  |  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  | H |  | Check Valve |  |  |  |  | 3
| Total Rej. Heat (MBH) |  |  | 181.419 |  | Suction Filter -- Group 1 |  | BTAS525 |  | Subcooler |  |  | B80x20 |  |  | Dia. x Length |  | 12x48 |  | Solenoid
3 | Heat Reclaim Avail. (MBH) |  |  | 90.7095 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out |  |  | 50º |  |  | Lbs @ 90% PD |  |  |  | C P R |  |  |  |  | 3
| Compressor Capacity (Tons) |  |  | 9.3 |  | Drier |  | C967 |  | TEV |  |  | Dual | [6 empty] | From / To
3 | Rack Size | [23 empty] | 3
Estimated Rack Weight Lbs.
3 | [24 empty] | 3

## Remodel Rack A
4 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Display Systems | 4
| 2016 Gees Mill Road |  |  |  | Location: |  |  |  |  | Rack Model: | 0 | [12 empty] | 1925 Ruffin Mill Road
4 | Conyers, Georgia 30013 |  |  |  | Store #: |  |  |  |  | Salesman | 0 | [12 empty] | Colonial Heights, VA 23834 | 4
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: |  |  |  |  | Prepared By: |  |  | Date Originated | [10 empty] | (804) 526-4455, Fax: (804) 526-1926
4 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC |  | 4
| 0 | 0 | 0 | 0 | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
4 | 0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
| 0 | 0 | 0 | 0 | [7 empty] | MCA |  |  |  | 10 |  |  | Fixture Plan:
4 | 0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | #N/A | [8 empty] | 4
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
4 | Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 4 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 4Sat | 4Sat2
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
4 | Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  |  |  | 4 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. | [5 empty] | COMP4SAT | COMP4SAT2
4 | Outside Air Temp. |  |  | 100 | [16 empty] | F P I |  |  |  | 4 |  | 0 | 0
| Required Load Group 1 |  |  | 0 | [16 empty] | Voltage | [5 empty] | 0 | 0
4 | Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA |  |  |  | 4 |  | 0 | 0
1 | Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA | [5 empty] | 0 | 0 | 0 | MBTUH_COMP4
4 | % Excess Capacity Group 1 | [19 empty] | MOPD |  |  |  | 4 |  | 0 | 0 | 0 | MBTUH_COMP4SAT
1.38 | Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight | [5 empty] | 0 | 0 | 0 | MBTUH_COMP4SAT2
4 |  |  |  | 0 | [16 empty] | Size |  |  |  | 4 |  | 0 | 0 | 0 | MBTUH_COMP4MAIN
0 | Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans | [5 empty] | 0 | 0
4 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  |  |  | 4 |  | 0 | 0
| Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From | [5 empty] | 0 | 0
4 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 4
0 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT |  |  |  |  | 0
4 |  |  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  |  |  |  | 4
0 | Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
4 | Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From | [8 empty] | 4
| Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
4 | % Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3 | 4
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
4 |  |  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve |  |  |  |  | 4
| Total Rej. Heat (MBH) |  |  | 0 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
4 | Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R |  |  |  |  | 4
| Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
4 | Rack Size | [23 empty] | 4
Estimated Rack Weight Lbs.
4 | [24 empty] | 4

## Remodel Rack B
5 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | [13 empty] | Display Systems | 5
| 2016 Gees Mill Road |  |  |  | Location: |  |  |  |  | Rack Model: | 0 | [12 empty] | 1925 Ruffin Mill Road
5 | Conyers, Georgia 30013 |  |  |  | Store #: |  |  |  |  | Salesman | 0 | [12 empty] | Colonial Heights, VA 23834 | 5
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: |  |  |  |  | Prepared By: |  |  | Date Originated | [10 empty] | (804) 526-4455, Fax: (804) 526-1926
5 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC |  | 5
| 0 | 0 | 0 | 0 | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
5 | 0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
| 0 | 0 | 0 | 0 | [7 empty] | MCA |  |  |  | 10 |  |  | Fixture Plan:
5 | 0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | #N/A | [8 empty] | 5
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
5 | Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 5 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 5Sat | 5Sat2
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
5 | Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  |  |  | 5 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. | [5 empty] | COMP5SAT | COMP5SAT2
5 | Outside Air Temp. |  |  | 100 | [16 empty] | F P I |  |  |  | 5 |  | 0 | 0
| Required Load Group 1 |  |  | 0 | [16 empty] | Voltage | [5 empty] | 0 | 0
5 | Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA |  |  |  | 5 |  | 0 | 0
1 | Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA | [5 empty] | 0 | 0 | 0 | MBTUH_COMP5
5 | % Excess Capacity Group 1 | [19 empty] | MOPD |  |  |  | 5 |  | 0 | 0 | 0 | MBTUH_COMP5SAT
1.35 | Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight | [5 empty] | 0 | 0 | 0 | MBTUH_COMP5SAT2
5 |  |  |  | 0 | [16 empty] | Size |  |  |  | 5 |  | 0 | 0 | 0 | MBTUH_COMP5MAIN
0 | Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans | [5 empty] | 0 | 0
5 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  |  |  | 5 |  | 0 | 0
| Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From | [5 empty] | 0 | 0
5 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 5
0 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT |  |  |  |  | 0
5 |  |  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  |  |  |  | 5
0 | Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
5 | Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From | [8 empty] | 5
| Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
5 | % Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3 | 5
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
5 |  |  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve |  |  |  |  | 5
| Total Rej. Heat (MBH) |  |  | 0 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
5 | Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R |  |  |  |  | 5
| Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
5 | Rack Size | [23 empty] | 5
Estimated Rack Weight Lbs.
5 | [24 empty] | 5

## Remodel Rack C
6 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack C | [13 empty] | Display Systems | 6
| 2016 Gees Mill Road |  |  |  | Location: |  |  |  |  | Rack Model: | 0 | [12 empty] | 1925 Ruffin Mill Road
6 | Conyers, Georgia 30013 |  |  |  | Store #: |  |  |  |  | Salesman | 0 | [12 empty] | Colonial Heights, VA 23834 | 6
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: |  |  |  |  | Prepared By: |  |  | Date Originated | [10 empty] | (804) 526-4455, Fax: (804) 526-1926
6 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC |  | 6
| 0 | 0 | 0 | 0 | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
6 | 0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
| 0 | 0 | 0 | 0 | [7 empty] | MCA |  |  |  | 10 |  |  | Fixture Plan:
6 | 0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | #N/A | [8 empty] | 6
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
6 | Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 6 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 6Sat | 6Sat2
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0 | MBTUH_6
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0 | MBTUH_6Sat
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0 | MBTUH_6Sat2
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0 | MBTUH_6Main
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
6 | Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  |  |  | 6 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  | 110 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. | [5 empty] | COMP6SAT | COMP6SAT2
6 | Outside Air Temp. |  |  | 100 | [16 empty] | F P I |  |  |  | 6 |  | 0 | 0
| Required Load Group 1 |  |  | 0 | [16 empty] | Voltage | [5 empty] | 0 | 0
6 | Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA |  |  |  | 6 |  | 0 | 0
1.249 | Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA | [5 empty] | 0 | 0 |  | 0 | MBTUH_COMP6
6 | % Excess Capacity Group 1 | [19 empty] | MOPD |  |  |  | 6 |  | 0 | 0 |  | 0 | MBTUH_COMP6SAT
1.54 | Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight | [5 empty] | 0 | 0 |  | 0 | MBTUH_COMP6SAT2
6 |  |  |  | 0 | [16 empty] | Size |  |  |  | 6 |  | 0 | 0 |  | 0 | MBTUH_COMP6MAIN
0 | Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans | [5 empty] | 0 | 0
6 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  |  |  | 6 |  | 0 | 0
1.248 | Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From | [5 empty] | 0 | 0
6 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 6
1.54 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT |  |  |  |  | 0
6 |  |  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  |  |  |  | 6
0 | Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
6 | Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From | [8 empty] | 6
| Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
6 | % Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3 | 6
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve |  |  |  |  | 0
6 |  |  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve |  |  |  |  | 6
| Total Rej. Heat (MBH) |  |  | 0 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid |  |  |  |  | 0
6 | Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R |  |  |  |  | 6
| Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
6 | Rack Size | [23 empty] | 6
Estimated Rack Weight Lbs.
6 | [24 empty] | 6

## Rack D
7 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack D | [13 empty] | Display Systems | 7
| 2016 Gees Mill Road |  |  |  | Location: |  |  |  |  | Rack Model: | 0 | [12 empty] | 1925 Ruffin Mill Road
7 | Conyers, Georgia 30013 |  |  |  | Store #: |  |  |  |  | Salesman | 0 | [12 empty] | Colonial Heights, VA 23834 | 7
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: |  |  |  |  | Prepared By: |  |  | Date Originated | [10 empty] | (804) 526-4455, Fax: (804) 526-1926
7 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC |  | 7
| 0 | 0 | 0 | 0 | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
7 | 0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
| 0 | 0 | 0 | 0 | [7 empty] | MCA |  |  |  | 10 |  |  | Fixture Plan:
7 | 0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | #N/A | [8 empty] | 7
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
| Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 7 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 7Sat | 7Sat2
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0 | 0 | MBTUH_7Main
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
7 | Refrigerant Type |  |  | R22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  |  |  | 7 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  | 110 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. | [5 empty] | COMP7SAT | COMP7SAT2
7 | Outside Air Temp. |  |  | 100 | [16 empty] | F P I |  |  |  | 7 |  | 0 | 0
| Required Load Group 1 |  |  | 0 | [16 empty] | Voltage | [5 empty] | 0 | 0
7 | Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA |  |  |  | 7 |  | 0 | 0
1.24 | Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA | [5 empty] | 0 | 0 |  | 0 | MBTUH_COMP7
7 | % Excess Capacity Group 1 | [19 empty] | MOPD |  |  |  | 7 |  | 0 | 0 |  | 0 | MBTUH_COMP7SAT
1.64 | Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight | [5 empty] | 0 | 0 |  | 0 | MBTUH_COMP7SAT2
7 |  |  |  | 0 | [16 empty] | Size |  |  |  | 7 |  | 0 | 0 |  | 0 | MBTUH_COMP7MAIN
0 | Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans | [5 empty] | 0 | 0
7 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  |  |  | 7 |  | 0 | 0
1.24 | Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From | [5 empty] | 0 | 0
7 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 7
1.64 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT |  |  |  |  | 0
7 |  |  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  |  |  |  | 7
0 | Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
7 | Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From | [8 empty] | 7
| Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
7 | % Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3 | 7
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
7 |  |  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve |  |  |  |  | 7
| Total Rej. Heat (MBH) |  |  | 0 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
7 | Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R |  |  |  |  | 7
| Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
7 | Rack Size | [23 empty] | 7
Estimated Rack Weight Lbs.
7 | [24 empty] | 7

## Remodel Circuit Tags
| Qty |  | Qty |  | Qty |  | Qty
A1 | 0 | B1 | 0 | C1 | 0 | D1 | 0
A2 | 0 | B2 | 0 | C2 | 0 | D2 | 0
A3 | 0 | B3 | 0 | C3 | 0 | D3 | 0
A4 | 0 | B4 | 0 | C4 | 0 | D4 | 0
A5 | 0 | B5 | 0 | C5 | 0 | D5 | 0
A6 | 0 | B6 | 0 | C6 | 0 | D6 | 0
A7 | 0 | B7 | 0 | C7 | 0 | D7 | 0
A8 | 0 | B8 | 0 | C8 | 0 | D8 | 0
A9 | 0 | B9 | 0 | C9 | 0 | D9 | 0
A10 | 0 | B10 | 0 | C10 | 0 | D10 | 0
A11 | 0 | B11 | 0 | C11 | 0 | D11 | 0
A12 | 0 | B12 | 0 | C12 | 0 | D12 | 0
A13 | 0 | B13 | 0 | C13 | 0 | D13 | 0
A14 | 0 | B14 | 0 | C14 | 0 | D14 | 0
A15 | 0 | B15 | 0 | C15 | 0 | D15 | 0
A16 | 0 | B16 | 0 | C16 | 0 | D16 | 0
A17 | 0 | B17 | 0 | C17 | 0 | D17 | 0
A18 | 0 | B18 | 0 | C18 | 0 | D18 | 0
A19 | 0 | B19 | 0 | C19 | 0 | D19 | 0
A20 | 0 | B20 | 0 | C20 | 0 | D20 | 0
A21 | 0 | B21 | 0 | C21 | 0 | D21 | 0
A22 | 0 | B22 | 0 | C22 | 0 | D22 | 0
A23 | 0 | B23 | 0 | C23 | 0 | D23 | 0
A24 | 0 | B24 | 0 | C24 | 0 | D24 | 0
A25 | 0 | B25 | 0 | C25 | 0 | D25 | 0
A26 | 0 | B26 | 0 | C26 | 0 | D26 | 0
A27 | 0 | B27 | 0 | C27 | 0 | D27 | 0
A28 | 0 | B28 | 0 | C28 | 0 | D28 | 0
A29 | 0 | B29 | 0 | C29 | 0 | D29 | 0
A30 | 0 | B30 | 0 | C30 | 0 | D30 | 0
| 0 |  | 0 |  | 0 |  | 0
|  |  | Grand Total | 0

## Sheet 8
8 | Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | None | [13 empty] | Display Systems | 8
| 2016 Gees Mill Road |  |  |  | Location: | Kings Mountain, NC. |  |  |  | Rack Model: | 0 | [12 empty] | 1925 Ruffin Mill Road
8 | Conyers, Georgia 30013 |  |  |  | Store #: | 2654 |  |  |  | Salesman | 0 | [12 empty] | Colonial Heights, VA 23834 | 8
| (770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: | 92617 |  |  |  | Prepared By: | SYON |  | Date Originated |  |  | 7/30/2007 | [7 empty] | (804) 526-4455, Fax: (804) 526-1926
8 | Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: | [5 empty] | 8
| 0 | 0 | 0 | 0 | [7 empty] | Line | [6 empty] | Single or Dual Point Pwr:
8 | 0 | 0 | 0 | 0 | [7 empty] | Control | [6 empty] | Case Manufacturer
| 0 | 0 | 0 | 0 | [7 empty] | MCA | [16 empty] | 1 | 2 | 3
8 | 0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent | [12 empty] | 8 |  |  | 0 |  | 1 | 2
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
8 | Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid | 8 | MBTUH_ | MBTUH_
| No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz |  | 8Sat | 8Sat2
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
[15 empty] | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 0 | 0
|  | General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
8 | Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model # |  |  |  | 8 |  | MBTUH_ | MBTUH_
| Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D. | [5 empty] | COMP8SAT | COMP8SAT2
8 | Outside Air Temp. |  |  | 100 | [16 empty] | F P I |  |  |  | 8 |  | 0 | 0
| Required Load Group 1 |  |  | 0 | [16 empty] | Voltage | [5 empty] | 0 | 0
8 | Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA |  |  |  | 8 |  | 0 | 0
| Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA | [5 empty] | 0 | 0 |  | 0 | MBTUH_COMP8
8 | % Excess Capacity Group 1 | [19 empty] | MOPD |  |  |  | 8 |  | 0 | 0 |  | 0 | MBTUH_COMP8SAT
1.54 | Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight | [5 empty] | 0 | 0 |  | 0 | MBTUH_COMP8SAT2
8 |  |  |  | 0 | [16 empty] | Size |  |  |  | 8 |  | 0 | 0 |  | 0 | MBTUH_COMP8MAIN
0 | Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans | [5 empty] | 0 | 0
8 | Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  |  |  | 8 |  | 0 | 0
| Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From | [5 empty] | 0 | 0
8 | % Excess Capacity Group 2 | [8 empty] | Rack Components | [14 empty] | 8
0 | Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
8 |  |  |  | 0 |  | Disch. Check Valve |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  |  |  |  | 8
0 | Required Load Group 3 |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Solenoid | [5 empty] | Line size To
8 | Comp. Capacity Group 3 |  |  | 0 |  | Bypass Regulator |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  |  |  | Suction Crossover / Load Shed |  |  |  |  | 8
| Effective capac. with subcooling |  |  | 0 |  | Oil type |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Group |  | 1 | 2 | 3
8 | % Excess Capacity Group 3 |  |  |  |  | Brand / Number |  |  |  | Surge Style | [9 empty] | Ball Valve |  |  |  |  | 8
| Rej. Heat (MBH) Group 3 |  |  | 0 |  | Resvr. Cap\CK VLV # |  |  |  | Attron | [5 empty] | Receiver H / V |  |  |  | Check Valve
8 |  |  |  | 0 |  | Suction Filter Main / Ind |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid |  |  |  |  | 8
| Total Rej. Heat (MBH) |  |  | 0 |  | Suction Accum. |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
8 | Heat Reclaim Avail. (MBH) |  |  | 0 |  | Drier / S.G. |  |  |  | TEV | [5 empty] | Analog Probe |  |  |  | From / To |  |  |  |  | 8
| Compressor Capacity (Tons) |  |  | 0
8 | Rack Size | [23 empty] | 8
Estimated Rack Weight
8 | [24 empty] | 8

## LOAD & PAGE SELECTION
Calculations of MBTUH Load & Page Selection
Total MBTUH (by rack)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Name | Rack | Value | If Match |  | Rack A | Rack B | Rack A +15 | Rack B +20 | Rack C | Rack D | None
Rack A | 1 | 464.932 | TRUE | 2: 464.932
Rack A | 2 | 121.42 | FALSE | 2: 121.42
Rack B | 3 | 148.343 | FALSE | 3: 148.343
Rack A +15 | 4 | 0 | FALSE | 4: 0
Rack B +20 | 5 | 0 | FALSE | 5: 0
Rack C | 6 | 0 | FALSE | 6: 0
Rack D | 7 | 0 | FALSE | 7: 0
None | 8 | 0 | FALSE | 8: 0
|  |  |  | 0 | 586.352 | 148.343 | 0 | 0 | 0 | 0 | 0
|  |  | Total | 2: 586.352; 3: 148.343
Total MBTUH Available (by compressor)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Name | Rack | Value | If Match |  | Rack A | Rack B | Rack A +15 | Rack B +20 | Rack C | Rack D | None
Rack A | 1 | 0 | TRUE | 2: 0
Rack A | 2 | 651 | FALSE | 2: 651
Rack B | 3 | 111.3 | FALSE | 3: 111.3
Rack A +15 | 4 | 0 | FALSE | 4: 0
Rack B +20 | 5 | 0 | FALSE | 5: 0
Rack C | 6 | 0 | FALSE | 6: 0
Rack D | 7 | 0 | FALSE | 7: 0
None | 8 | 0 | FALSE | 8: 0
|  |  |  | 0 | 651 | 111.3 | 0 | 0 | 0 | 0 | 0
|  |  | Total | 2: 651; 3: 111.3
Total Satellite MBTUH (by rack)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Name | Rack | Value | If Match |  | Rack A | Rack B | Rack A +15 | Rack B +20 | Rack C | Rack D | None
Rack A | 1 | 0 | TRUE | 2: 0
Rack A | 2 | 0 | FALSE | 2: 0
Rack B | 3 | 0 | FALSE | 3: 0
Rack A +15 | 4 | 0 | FALSE | 4: 0
Rack B +20 | 5 | 0 | FALSE | 5: 0
Rack C | 6 | 0 | FALSE | 6: 0
Rack D | 7 | 0 | FALSE | 7: 0
None | 8 | 0 | FALSE | 8: 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total
Total Satellite MBTUH Available (by compressor)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Name | Rack | Value | If Match |  | Rack A | Rack B | Rack A +15 | Rack B +20 | Rack C | Rack D | None
Rack A | 1 | 0 | TRUE | 2: 0
Rack A | 2 | 0 | FALSE | 2: 0
Rack B | 3 | 0 | FALSE | 3: 0
Rack A +15 | 4 | 0 | FALSE | 4: 0
Rack B +20 | 5 | 0 | FALSE | 5: 0
Rack C | 6 | 0 | FALSE | 6: 0
Rack D | 7 | 0 | FALSE | 7: 0
None | 8 | 0 | FALSE | 8: 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total
Total Satellite 2 MBTUH (by rack)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Name | Rack | Value | If Match |  | Rack A | Rack B | Rack A +15 | Rack B +20 | Rack C | Rack D | None
Rack A | 1 | 0 | TRUE | 2: 0
Rack A | 2 | 0 | FALSE | 2: 0
Rack B | 3 | 0 | FALSE | 3: 0
Rack A +15 | 4 | 0 | FALSE | 4: 0
Rack B +20 | 5 | 0 | FALSE | 5: 0
Rack C | 6 | 0 | FALSE | 6: 0
Rack D | 7 | 0 | FALSE | 7: 0
None | 8 | 0 | FALSE | 8: 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total
Total Satellite 2 MBTUH Available (by compressor)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Name | Rack | Value | If Match |  | Rack A | Rack B | Rack A +15 | Rack B +20 | Rack C | Rack D | None
Rack A | 1 | 0 | TRUE | 2: 0
Rack A | 2 | 0 | FALSE | 2: 0
Rack B | 3 | 0 | FALSE | 3: 0
Rack A +15 | 4 | 0 | FALSE | 4: 0
Rack B +20 | 5 | 0 | FALSE | 5: 0
Rack C | 6 | 0 | FALSE | 6: 0
Rack D | 7 | 0 | FALSE | 7: 0
None | 8 | 0 | FALSE | 8: 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total
Total Tons (from available)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
[5 empty] | 651 | 111.3
|  |  | Sum | 0 | 651 | 111.3 | 0 | 0 | 0 | 0 | 0
|  |  | Tons | 0 | 54.3 | 9.3 | 0 | 0 | 0 | 0 | 0

## CIRLOOK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
|  | DX6LD MD Door Produce, Deli, Meat, Dairy, Beer | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4DX6LD |  | 4' | 4' DX6LD | 1 |  | MD Door | 1.188 | 28 | Off Cycle | 115 | 0.1 | 0.96 | 0.61 | 12 | 115.2 | 73.2 |  |  | SORIT 12 | [5 empty] | 3 | 4 | 8 | 9 | 12 |  | 13 | 14 | 15 | 16 | 17
[8 empty] | 28 | [18 empty] | MBTUH | EVAP | FAN | VOLT | LIGHT | A/S | FAN | LIGHT | A/S
8DX6LD |  | 8' | 8' DX6LD | 1 |  | MD Door | 2.376 | 28 | Off Cycle | 115 | 0.2 | 1.44 | 1.22 | 24 | 172.8 | 146.4 |  |  | SORIT 12
12DX6LD |  | 12' | 12' DX6LD | 1 |  | MD Door | 3.564 | 28 | Off Cycle | 115 | 0.4 | 1.82 | 1.82 | 48 | 218.4 | 218.4 |  |  | SORIT 12
8'8DX6LD |  | 8'8' | 16' DX6LD | 1 |  | MD Door | 4.752 | 28 | Off Cycle | 115 | 0.4 | 2.88 | 2.44 | 48 | 345.6 | 292.8 |  |  | SORIT 12
8'12DX6LD |  | 8'12' | 20' DX6LD | 1 |  | MD Door | 5.94 | 28 | Off Cycle | 115 | 0.6 | 3.26 | 3.04 | 72 | 391.2 | 364.8 |  |  | SORIT 12
8'8'8DX6LD |  | 8'8'8' | 24' DX6LD | 1 |  | MD Door | 7.128 | 28 | Off Cycle | 115 | 0.6 | 4.32 | 3.66 | 72 | 518.4 | 439.2 |  |  | SORIT 12
12'12DX6LD |  | 12'12' | 24' DX6LD | 1 |  | MD Door | 7.128 | 28 | Off Cycle | 115 | 0.8 | 3.64 | 3.64 | 96 | 436.8 | 436.8 |  |  | SORIT 12
8'8'12DX6LD |  | 8'8'12' | 28' DX6LD | 1 |  | MD Door | 8.316 | 28 | Off Cycle | 115 | 0.8 | 4.7 | 4.26 | 96 | 564 | 511.2 |  |  | SORIT 12
8'8'8'8DX6LD |  | 8'8'8'8' | 32' DX6LD | 1 |  | MD Door | 9.504 | 28 | Off Cycle | 115 | 0.8 | 5.76 | 4.88 | 96 | 691.2 | 585.6 |  |  | SORIT 12
8'12'12DX6LD |  | 8'12'12' | 32' DX6LD | 1 |  | MD Door | 9.504 | 28 | Off Cycle | 115 | 1 | 5.08 | 4.86 | 120 | 609.6 | 583.2 |  |  | SORIT 12 |  |  |  |  | TOTAL |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
8'8'8'12DX6LD |  | 8'8'8'12' | 36' DX6LD | 1 |  | MD Door | 10.692 | 28 | Off Cycle | 115 | 1 | 6.14 | 5.48 | 120 | 736.8 | 657.6 |  |  | SORIT 12
12'12'12DX6LD |  | 12'12'12' | 36' DX6LD | 1 |  | MD Door | 10.692 | 28 | Off Cycle | 115 | 1.2 | 5.46 | 5.46 | 144 | 655.2 | 655.2 |  |  | SORIT 12
8'8'8'8'8DX6LD |  | 8'8'8'8'8' | 40' DX6LD | 1 |  | MD Door | 11.88 | 28 | Off Cycle | 115 | 1 | 7.2 | 6.1 | 120 | 864 | 732 |  |  | SORIT 12
8'8'12'12DX6LD |  | 8'8'12'12' | 40' DX6LD | 1 |  | MD Door | 11.88 | 28 | Off Cycle | 115 | 1.2 | 6.52 | 6.08 | 144 | 782.4 | 729.6 |  |  | SORIT 12
8'8'8'8'12DX6LD |  | 8'8'8'8'12' | 44' DX6LD | 1 |  | MD Door | 13.068 | 28 | Off Cycle | 115 | 1.2 | 7.58 | 6.7 | 144 | 909.6 | 804 |  |  | SORIT 12
8'12'12'12DX6LD |  | 8'12'12'12' | 44' DX6LD | 1 |  | MD Door | 13.068 | 28 | Off Cycle | 115 | 1.4 | 6.9 | 6.68 | 168 | 828 | 801.6 |  |  | SORIT 12
8'8'8'12'12DX6LD |  | 8'8'8'12'12' | 48' DX6LD | 1 |  | MD Door | 14.256 | 28 | Off Cycle | 115 | 1.4 | 7.96 | 7.3 | 168 | 955.2 | 876 |  |  | SORIT 12
12'12'12'12DX6LD |  | 12'12'12'12' | 48' DX6LD | 1 |  | MD Door | 14.256 | 28 | Off Cycle | 115 | 1.6 | 7.28 | 7.28 | 192 | 873.6 | 873.6 |  |  | SORIT 12
8'8'12'12'12DX6LD |  | 8'8'12'12'12' | 52' DX6LD | 1 |  | MD Door | 15.444 | 28 | Off Cycle | 115 | 1.6 | 8.34 | 7.9 | 192 | 1000.8 | 948 |  |  | SORIT 12
8'12'12'12'12DX6LD |  | 8'12'12'12'12 | 56' DX6LD | 1 |  | MD Door | 16.632 | 28 | Off Cycle | 115 | 1.8 | 8.72 | 8.5 | 216 | 1046.4 | 1020 |  |  | SORIT 12
|  | DX6UD MD Door Produce, Deli, Meat, Dairy, Beer | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4DX6UD |  | 4' | 4' DX6UD | 1 |  | MD Door | 1.024 | 28 | Off Cycle | 115 | 0.1 | 0.96 | 0.61 | 12 | 115.2 | 73.2 |  |  | SORIT 12
28
8DX6UD |  | 8' | 8' DX6UD | 1 |  | MD Door | 2.048 | 28 | Off Cycle | 115 | 0.2 | 1.44 | 1.22 | 24 | 172.8 | 146.4 |  |  | SORIT 12
12DX6UD |  | 12' | 12' DX6UD | 1 |  | MD Door | 3.072 | 28 | Off Cycle | 115 | 0.4 | 1.82 | 1.82 | 48 | 218.4 | 218.4 |  |  | SORIT 12
8'8DX6UD |  | 8'8' | 16' DX6UD | 1 |  | MD Door | 4.096 | 28 | Off Cycle | 115 | 0.4 | 2.88 | 2.44 | 48 | 345.6 | 292.8 |  |  | SORIT 12
8'12DX6UD |  | 8'12' | 20' DX6UD | 1 |  | MD Door | 5.12 | 28 | Off Cycle | 115 | 0.6 | 3.26 | 3.04 | 72 | 391.2 | 364.8 |  |  | SORIT 12
8'8'8DX6UD |  | 8'8'8' | 24' DX6UD | 1 |  | MD Door | 6.144 | 28 | Off Cycle | 115 | 0.6 | 4.32 | 3.66 | 72 | 518.4 | 439.2 |  |  | SORIT 12
12'12DX6UD |  | 12'12' | 24' DX6UD | 1 |  | MD Door | 6.144 | 28 | Off Cycle | 115 | 0.8 | 3.64 | 3.64 | 96 | 436.8 | 436.8 |  |  | SORIT 12
8'8'12DX6UD |  | 8'8'12' | 28' DX6UD | 1 |  | MD Door | 7.168 | 28 | Off Cycle | 115 | 0.8 | 4.7 | 4.26 | 96 | 564 | 511.2 |  |  | SORIT 12
8'8'8'8DX6UD |  | 8'8'8'8' | 32' DX6UD | 1 |  | MD Door | 8.192 | 28 | Off Cycle | 115 | 0.8 | 5.76 | 4.88 | 96 | 691.2 | 585.6 |  |  | SORIT 12
8'12'12DX6UD |  | 8'12'12' | 32' DX6UD | 1 |  | MD Door | 8.192 | 28 | Off Cycle | 115 | 1 | 5.08 | 4.86 | 120 | 609.6 | 583.2 |  |  | SORIT 12
8'8'8'12DX6UD |  | 8'8'8'12' | 36' DX6UD | 1 |  | MD Door | 9.216 | 28 | Off Cycle | 115 | 1 | 6.14 | 5.48 | 120 | 736.8 | 657.6 |  |  | SORIT 12
12'12'12DX6UD |  | 12'12'12' | 36' DX6UD | 1 |  | MD Door | 9.216 | 28 | Off Cycle | 115 | 1.2 | 5.46 | 5.46 | 144 | 655.2 | 655.2 |  |  | SORIT 12
8'8'8'8'8DX6UD |  | 8'8'8'8'8' | 40' DX6UD | 1 |  | MD Door | 10.24 | 28 | Off Cycle | 115 | 1 | 7.2 | 6.1 | 120 | 864 | 732 |  |  | SORIT 12
8'8'12'12DX6UD |  | 8'8'12'12' | 40' DX6UD | 1 |  | MD Door | 10.24 | 28 | Off Cycle | 115 | 1.2 | 6.52 | 6.08 | 144 | 782.4 | 729.6 |  |  | SORIT 12
8'8'8'8'12DX6UD |  | 8'8'8'8'12' | 44' DX6UD | 1 |  | MD Door | 11.264 | 28 | Off Cycle | 115 | 1.2 | 7.58 | 6.7 | 144 | 909.6 | 804 |  |  | SORIT 12
8'12'12'12DX6UD |  | 8'12'12'12' | 44' DX6UD | 1 |  | MD Door | 11.264 | 28 | Off Cycle | 115 | 1.4 | 6.9 | 6.68 | 168 | 828 | 801.6 |  |  | SORIT 12
8'8'8'12'12DX6UD |  | 8'8'8'12'12' | 48' DX6UD | 1 |  | MD Door | 12.288 | 28 | Off Cycle | 115 | 1.4 | 7.96 | 7.3 | 168 | 955.2 | 876 |  |  | SORIT 12
12'12'12'12DX6UD |  | 12'12'12'12' | 48' DX6UD | 1 |  | MD Door | 12.288 | 28 | Off Cycle | 115 | 1.6 | 7.28 | 7.28 | 192 | 873.6 | 873.6 |  |  | SORIT 12
8'8'12'12'12DX6UD |  | 8'8'12'12'12' | 52' DX6UD | 1 |  | MD Door | 13.312 | 28 | Off Cycle | 115 | 1.6 | 8.34 | 7.9 | 192 | 1000.8 | 948 |  |  | SORIT 12
8'12'12'12'12DX6UD |  | 8'12'12'12'12 | 56' DX6UD | 1 |  | MD Door | 14.336 | 28 | Off Cycle | 115 | 1.8 | 8.72 | 8.5 | 216 | 1046.4 | 1020 |  |  | SORIT 12
|  | DX6LN Produce, Dairy, HMS and Beverage | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4DX6LN |  | 4' | 4' DX6LN | 1 |  | MD Dairy | 4.74 | 28 | Off Cycle | 115 | 0.1 | 0.6 | 0 | 12 | 72 | 0 |  |  | SORIT 12
6DX6LN |  | 6' | 6' DX6LN | 1 |  | MD Dairy | 7.11 | 28 | Off Cycle | 115 | 0.2 | 1.1 | 0 | 24 | 132 | 0 |  |  | SORIT 12
8DX6LN |  | 8' | 8' DX6LN | 1 |  | MD Dairy | 9.48 | 28 | Off Cycle | 115 | 0.2 | 1.2 | 0 | 24 | 144 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12DX6LN |  | 12' | 12' DX6LN | 1 |  | MD Dairy | 14.22 | 28 | Off Cycle | 115 | 0.4 | 1.9 | 0 | 48 | 228 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8DX6LN |  | 8'8' | 16' DX6LN | 1 |  | MD Dairy | 18.96 | 28 | Off Cycle | 115 | 0.4 | 2.4 | 0 | 48 | 288 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12DX6LN |  | 8'12' | 20' DX6LN | 1 |  | MD Dairy | 23.7 | 28 | Off Cycle | 115 | 0.6 | 3.1 | 0 | 72 | 372 | 0 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8DX6LN |  | 8'8'8' | 24' DX6LN | 1 |  | MD Dairy | 28.44 | 28 | Off Cycle | 115 | 0.6 | 3.6 | 0 | 72 | 432 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12DX6LN |  | 12'12' | 24' DX6LN | 1 |  | MD Dairy | 28.44 | 28 | Off Cycle | 115 | 0.8 | 3.8 | 0 | 96 | 456 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'12DX6LN |  | 8'8'12' | 28' DX6LN | 1 |  | MD Dairy | 33.18 | 28 | Off Cycle | 115 | 0.8 | 4.3 | 0 | 96 | 516 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8DX6LN |  | 8'8'8'8' | 32' DX6LN | 1 |  | MD Dairy | 37.92 | 28 | Off Cycle | 115 | 0.8 | 4.8 | 0 | 96 | 576 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'12'12DX6LN |  | 8'12'12' | 32' DX6LN | 1 |  | MD Dairy | 37.92 | 28 | Off Cycle | 115 | 1 | 5 | 0 | 120 | 600 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'12DX6LN |  | 8'8'8'12' | 36' DX6LN | 1 |  | MD Dairy | 42.66 | 28 | Off Cycle | 115 | 1 | 5.5 | 0 | 120 | 660 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
12'12'12DX6LN |  | 12'12'12' | 36' DX6LN | 1 |  | MD Dairy | 42.66 | 28 | Off Cycle | 115 | 1.2 | 5.7 | 0 | 144 | 684 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'8'8DX6LN |  | 8'8'8'8'8' | 40' DX6LN | 1 |  | MD Dairy | 47.4 | 28 | Off Cycle | 115 | 1 | 6 | 0 | 120 | 720 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12DX6LN |  | 8'8'12'12' | 40' DX6LN | 1 |  | MD Dairy | 47.4 | 28 | Off Cycle | 115 | 1.2 | 6.2 | 0 | 144 | 744 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12DX6LN |  | 8'8'8'8'12' | 44' DX6LN | 1 |  | MD Dairy | 52.14 | 28 | Off Cycle | 115 | 1.2 | 6.7 | 0 | 144 | 804 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12DX6LN |  | 8'12'12'12' | 44' DX6LN | 1 |  | MD Dairy | 52.14 | 28 | Off Cycle | 115 | 1.4 | 6.9 | 0 | 168 | 828 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12DX6LN |  | 8'8'8'12'12' | 48' DX6LN | 1 |  | MD Dairy | 56.88 | 28 | Off Cycle | 115 | 1.4 | 7.4 | 0 | 168 | 888 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12DX6LN |  | 12'12'12'12' | 48' DX6LN | 1 |  | MD Dairy | 56.88 | 28 | Off Cycle | 115 | 1.6 | 7.6 | 0 | 192 | 912 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12DX6LN |  | 8'8'12'12'12' | 52' DX6LN | 1 |  | MD Dairy | 61.62 | 28 | Off Cycle | 115 | 1.6 | 8.1 | 0 | 192 | 972 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12DX6LN |  | 8'12'12'12'12 | 56' DX6LN | 1 |  | MD Dairy | 66.36 | 28 | Off Cycle | 115 | 1.8 | 8.8 | 0 | 216 | 1056 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | DX6XN Deli Meat | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4DX6XN |  | 4' | 4' DX6XN | 1 |  | MD Deli Meat | 4.416 | 28 | Off Cycle | 115 | 0.1 | 0.6 | 0 | 12 | 72 | 0 |  |  | SORIT 12
6DX6XN |  | 6' | 6' DX6XN | 1 |  | MD Deli Meat | 6.624 | 28 | Off Cycle | 115 | 0.2 | 1.1 | 0 | 24 | 132 | 0 |  |  | SORIT 12
8DX6XN |  | 8' | 8' DX6XN | 1 |  | MD Deli Meat | 8.832 | 28 | Off Cycle | 115 | 0.2 | 1.2 | 0 | 24 | 144 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12DX6XN |  | 12' | 12' DX6XN | 1 |  | MD Deli Meat | 13.248 | 28 | Off Cycle | 115 | 0.4 | 1.9 | 0 | 48 | 228 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8DX6XN |  | 8'8' | 16' DX6XN | 1 |  | MD Deli Meat | 17.664 | 28 | Off Cycle | 115 | 0.4 | 2.4 | 0 | 48 | 288 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12DX6XN |  | 8'12' | 20' DX6XN | 1 |  | MD Deli Meat | 22.08 | 28 | Off Cycle | 115 | 0.6 | 3.1 | 0 | 72 | 372 | 0 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8DX6XN |  | 8'8'8' | 24' DX6XN | 1 |  | MD Deli Meat | 26.496 | 28 | Off Cycle | 115 | 0.6 | 3.6 | 0 | 72 | 432 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12DX6XN |  | 12'12' | 24' DX6XN | 1 |  | MD Deli Meat | 26.496 | 28 | Off Cycle | 115 | 0.8 | 3.8 | 0 | 96 | 456 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'12DX6XN |  | 8'8'12' | 28' DX6XN | 1 |  | MD Deli Meat | 30.912 | 28 | Off Cycle | 115 | 0.8 | 4.3 | 0 | 96 | 516 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8DX6XN |  | 8'8'8'8' | 32' DX6XN | 1 |  | MD Deli Meat | 35.328 | 28 | Off Cycle | 115 | 0.8 | 4.8 | 0 | 96 | 576 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'12'12DX6XN |  | 8'12'12' | 32' DX6XN | 1 |  | MD Deli Meat | 35.328 | 28 | Off Cycle | 115 | 1 | 5 | 0 | 120 | 600 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'12DX6XN |  | 8'8'8'12' | 36' DX6XN | 1 |  | MD Deli Meat | 39.744 | 28 | Off Cycle | 115 | 1 | 5.5 | 0 | 120 | 660 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
12'12'12DX6XN |  | 12'12'12' | 36' DX6XN | 1 |  | MD Deli Meat | 39.744 | 28 | Off Cycle | 115 | 1.2 | 5.7 | 0 | 144 | 684 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'8'8DX6XN |  | 8'8'8'8'8' | 40' DX6XN | 1 |  | MD Deli Meat | 44.16 | 28 | Off Cycle | 115 | 1 | 6 | 0 | 120 | 720 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12DX6XN |  | 8'8'12'12' | 40' DX6XN | 1 |  | MD Deli Meat | 44.16 | 28 | Off Cycle | 115 | 1.2 | 6.2 | 0 | 144 | 744 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12DX6XN |  | 8'8'8'8'12' | 44' DX6XN | 1 |  | MD Deli Meat | 48.576 | 28 | Off Cycle | 115 | 1.2 | 6.7 | 0 | 144 | 804 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12DX6XN |  | 8'12'12'12' | 44' DX6XN | 1 |  | MD Deli Meat | 48.576 | 28 | Off Cycle | 115 | 1.4 | 6.9 | 0 | 168 | 828 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12DX6XN |  | 8'8'8'12'12' | 48' DX6XN | 1 |  | MD Deli Meat | 52.992 | 28 | Off Cycle | 115 | 1.4 | 7.4 | 0 | 168 | 888 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12DX6XN |  | 12'12'12'12' | 48' DX6XN | 1 |  | MD Deli Meat | 52.992 | 28 | Off Cycle | 115 | 1.6 | 7.6 | 0 | 192 | 912 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12DX6XN |  | 8'8'12'12'12' | 52' DX6XN | 1 |  | MD Deli Meat | 57.408 | 28 | Off Cycle | 115 | 1.6 | 8.1 | 0 | 192 | 972 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12DX6XN |  | 8'12'12'12'12 | 56' DX6XN | 1 |  | MD Deli Meat | 61.824 | 28 | Off Cycle | 115 | 1.8 | 8.8 | 0 | 216 | 1056 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | MX4HN MD FRESH MEAT, SEAFOOD | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4MX4HN |  | 4' | 4' MX4HN | 1 |  | MD Fresh Meat | 4.25 | 23 | Off Cycle | 115 | 0.14 | 1.25 | 0 | 16.8 | 150 | 0
6MX4HN |  | 6' | 6' MX4HN | 1 |  | MD Fresh Meat | 6.382 | 23 | Off Cycle | 115 | 0.28 | 2.2 | 0 | 33.6 | 264 | 0
8MX4HN |  | 8' | 8' MX4HN | 1 |  | MD Fresh Meat | 8.506 | 23 | Off Cycle | 115 | 0.28 | 2.5 | 0 | 33.6 | 300 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12MX4HN |  | 12' | 12' MX4HN | 1 |  | MD Fresh Meat | 12.754 | 23 | Off Cycle | 115 | 0.56 | 3.8 | 0 | 67.2 | 456 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8MX4HN |  | 8'8' | 16' MX4HN | 1 |  | MD Fresh Meat | 17.012 | 23 | Off Cycle | 115 | 0.56 | 5 | 0 | 67.2 | 600 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12MX4HN |  | 8'12' | 20' MX4HN | 1 |  | MD Fresh Meat | 21.26 | 23 | Off Cycle | 115 | 0.84 | 6.3 | 0 | 100.8 | 756 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8MX4HN |  | 8'8'8' | 24' MX4HN | 1 |  | MD Fresh Meat | 25.518 | 23 | Off Cycle | 115 | 0.84 | 7.5 | 0 | 100.8 | 900 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12MX4HN |  | 12'12' | 24' MX4HN | 1 |  | MD Fresh Meat | 25.508 | 23 | Off Cycle | 115 | 1.12 | 7.6 | 0 | 134.4 | 912 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'12MX4HN |  | 8'8'12' | 28' MX4HN | 1 |  | MD Fresh Meat | 29.766 | 23 | Off Cycle | 115 | 1.12 | 8.8 | 0 | 134.4 | 1056 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8MX4HN |  | 8'8'8'8' | 32' MX4HN | 1 |  | MD Fresh Meat | 34.024 | 23 | Off Cycle | 115 | 1.12 | 10 | 0 | 134.4 | 1200 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'12'12MX4HN |  | 8'12'12' | 32' MX4HN | 1 |  | MD Fresh Meat | 34.014 | 23 | Off Cycle | 115 | 1.4 | 10.1 | 0 | 168 | 1212 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'12MX4HN |  | 8'8'8'12' | 36' MX4HN | 1 |  | MD Fresh Meat | 38.272 | 23 | Off Cycle | 115 | 1.4 | 11.3 | 0 | 168 | 1356 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
12'12'12MX4HN |  | 12'12'12' | 36' MX4HN | 1 |  | MD Fresh Meat | 38.262 | 23 | Off Cycle | 115 | 1.68 | 11.4 | 0 | 201.6 | 1368 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'8'8MX4HN |  | 8'8'8'8'8' | 40' MX4HN | 1 |  | MD Fresh Meat | 42.53 | 23 | Off Cycle | 115 | 1.4 | 12.5 | 0 | 168 | 1500 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12MX4HN |  | 8'8'12'12' | 40' MX4HN | 1 |  | MD Fresh Meat | 42.52 | 23 | Off Cycle | 115 | 1.68 | 12.6 | 0 | 201.6 | 1512 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12MX4HN |  | 8'8'8'8'12' | 44' MX4HN | 1 |  | MD Fresh Meat | 46.778 | 23 | Off Cycle | 115 | 1.68 | 13.8 | 0 | 201.6 | 1656 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12MX4HN |  | 8'12'12'12' | 44' MX4HN | 1 |  | MD Fresh Meat | 46.768 | 23 | Off Cycle | 115 | 1.96 | 13.9 | 0 | 235.2 | 1668 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12MX4HN |  | 8'8'8'12'12' | 48' MX4HN | 1 |  | MD Fresh Meat | 51.026 | 23 | Off Cycle | 115 | 1.96 | 15.1 | 0 | 235.2 | 1812 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12MX4HN |  | 12'12'12'12' | 48' MX4HN | 1 |  | MD Fresh Meat | 51.016 | 23 | Off Cycle | 115 | 2.24 | 15.2 | 0 | 268.8 | 1824 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12MX4HN |  | 8'8'12'12'12' | 52' MX4HN | 1 |  | MD Fresh Meat | 55.274 | 23 | Off Cycle | 115 | 2.24 | 16.4 | 0 | 268.8 | 1968 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12MX4HN |  | 8'12'12'12'12 | 56' MX4HN | 1 |  | MD Fresh Meat | 59.522 | 23 | Off Cycle | 115 | 2.52 | 17.7 | 0 | 302.4 | 2124 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | MX5HN MD FRESH MEAT, SEAFOOD | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4MX5HN |  | 4' | 4' MX5HN | 1 |  | MD Fresh Meat | 5.632 | 23 | Off Cycle | 115 | 0.14 | 1.5 | 0 | 16.8 | 180 | 0
6MX5HN |  | 6' | 6' MX5HN | 1 |  | MD Fresh Meat | 8.448 | 23 | Off Cycle | 115 | 0.28 | 2.7 | 0 | 33.6 | 324 | 0
8MX5HN |  | 8' | 8' MX5HN | 1 |  | MD Fresh Meat | 11.264 | 23 | Off Cycle | 115 | 0.28 | 3 | 0 | 33.6 | 360 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12MX5HN |  | 12' | 12' MX5HN | 1 |  | MD Fresh Meat | 16.896 | 23 | Off Cycle | 115 | 0.56 | 4.5 | 0 | 67.2 | 540 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8MX5HN |  | 8'8' | 16' MX5HN | 1 |  | MD Fresh Meat | 22.528 | 23 | Off Cycle | 115 | 0.56 | 6 | 0 | 67.2 | 720 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12MX5HN |  | 8'12' | 20' MX5HN | 1 |  | MD Fresh Meat | 28.16 | 23 | Off Cycle | 115 | 0.84 | 7.5 | 0 | 100.8 | 900 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8MX5HN |  | 8'8'8' | 24' MX5HN | 1 |  | MD Fresh Meat | 33.792 | 23 | Off Cycle | 115 | 0.84 | 9 | 0 | 100.8 | 1080 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12MX5HN |  | 12'12' | 24' MX5HN | 1 |  | MD Fresh Meat | 33.792 | 23 | Off Cycle | 115 | 1.12 | 9 | 0 | 134.4 | 1080 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'12MX5HN |  | 8'8'12' | 28' MX5HN | 1 |  | MD Fresh Meat | 39.424 | 23 | Off Cycle | 115 | 1.12 | 10.5 | 0 | 134.4 | 1260 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8MX5HN |  | 8'8'8'8' | 32' MX5HN | 1 |  | MD Fresh Meat | 45.056 | 23 | Off Cycle | 115 | 1.12 | 12 | 0 | 134.4 | 1440 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'12'12MX5HN |  | 8'12'12' | 32' MX5HN | 1 |  | MD Fresh Meat | 45.056 | 23 | Off Cycle | 115 | 1.4 | 12 | 0 | 168 | 1440 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'12MX5HN |  | 8'8'8'12' | 36' MX5HN | 1 |  | MD Fresh Meat | 50.688 | 23 | Off Cycle | 115 | 1.4 | 13.5 | 0 | 168 | 1620 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
12'12'12MX5HN |  | 12'12'12' | 36' MX5HN | 1 |  | MD Fresh Meat | 50.688 | 23 | Off Cycle | 115 | 1.68 | 13.5 | 0 | 201.6 | 1620 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'8'8MX5HN |  | 8'8'8'8'8' | 40' MX5HN | 1 |  | MD Fresh Meat | 56.32 | 23 | Off Cycle | 115 | 1.4 | 15 | 0 | 168 | 1800 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12MX5HN |  | 8'8'12'12' | 40' MX5HN | 1 |  | MD Fresh Meat | 56.32 | 23 | Off Cycle | 115 | 1.68 | 15 | 0 | 201.6 | 1800 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12MX5HN |  | 8'8'8'8'12' | 44' MX5HN | 1 |  | MD Fresh Meat | 61.952 | 23 | Off Cycle | 115 | 1.68 | 16.5 | 0 | 201.6 | 1980 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12MX5HN |  | 8'12'12'12' | 44' MX5HN | 1 |  | MD Fresh Meat | 61.952 | 23 | Off Cycle | 115 | 1.96 | 16.5 | 0 | 235.2 | 1980 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12MX5HN |  | 8'8'8'12'12' | 48' MX5HN | 1 |  | MD Fresh Meat | 67.584 | 23 | Off Cycle | 115 | 1.96 | 18 | 0 | 235.2 | 2160 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12MX5HN |  | 12'12'12'12' | 48' MX5HN | 1 |  | MD Fresh Meat | 67.584 | 23 | Off Cycle | 115 | 2.24 | 18 | 0 | 268.8 | 2160 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12MX5HN |  | 8'8'12'12'12' | 52' MX5HN | 1 |  | MD Fresh Meat | 73.216 | 23 | Off Cycle | 115 | 2.24 | 19.5 | 0 | 268.8 | 2340 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12MX5HN |  | 8'12'12'12'12 | 56' MX5HN | 1 |  | MD Fresh Meat | 78.848 | 23 | Off Cycle | 115 | 2.52 | 21 | 0 | 302.4 | 2520 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | PX2XN PRODUCE |  | PRODUCE | [13 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4PX2XN |  | 4' | 4' PX2XN | 1 |  | Produce | 5.14 | 26 | Off Cycle | 115 | 0.1 | 0.5 |  | 12 | 60 | 0 |  |  | SORIT 12 |  |  | 1/2
6PX2XN |  | 6' | 6' PX2XN | 1 |  | Produce | 7.71 | 26 | Off Cycle | 115 | 0.2 | 0.88 |  | 24 | 105.6 | 0 |  |  | SORIT 12 |  |  | 5/8
8PX2XN |  | 8' | 8' PX2XN | 1 |  | Produce | 10.28 | 26 | Off Cycle | 115 | 0.2 | 1 |  | 24 | 120 | 0 |  |  | SORIT 12 |  |  | 1/2
12PX2XN |  | 12' | 12' PX2XN | 1 |  | Produce | 15.42 | 26 | Off Cycle | 115 | 0.4 | 1.5 |  | 48 | 180 | 0 |  |  | SORIT 12 |  |  | 5/8
8'8PX2XN |  | 8'8' | 16' PX2XN | 1 |  | Produce | 20.56 | 26 | Off Cycle | 115 | 0.4 | 2 |  | 48 | 240 | 0 |  |  | SORIT 12 |  |  | 5/8
8'12PX2XN |  | 8'12' | 20' PX2XN | 1 |  | Produce | 25.7 | 26 | Off Cycle | 115 | 0.6 | 2.5 |  | 72 | 300 | 0 |  |  | SORIT 15 |  |  | 7/8
8'8'8PX2XN |  | 8'8'8' | 24' PX2XN | 1 |  | Produce | 30.84 | 26 | Off Cycle | 115 | 0.6 | 3 |  | 72 | 360 | 0 |  |  | SORIT 15 |  |  | 7/8
12'12PX2XN |  | 12'12' | 24' PX2XN | 1 |  | Produce | 30.84 | 26 | Off Cycle | 115 | 0.8 | 3 |  | 96 | 360 | 0 |  |  | SORIT 15 |  |  | 7/8
8'8'12PX2XN |  | 8'8'12' | 28' PX2XN | 1 |  | Produce | 35.98 | 26 | Off Cycle | 115 | 0.8 | 3.5 |  | 96 | 420 | 0 |  |  | SORIT 15 |  |  | 7/8
8'8'8'8PX2XN |  | 8'8'8'8' | 32' PX2XN | 1 |  | Produce | 41.12 | 26 | Off Cycle | 115 | 0.8 | 4 |  | 96 | 480 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'12'12PX2XN |  | 8'12'12' | 32' PX2XN | 1 |  | Produce | 41.12 | 26 | Off Cycle | 115 | 1 | 4 |  | 120 | 480 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8'12PX2XN |  | 8'8'8'12' | 36' PX2XN | 1 |  | Produce | 46.26 | 26 | Off Cycle | 115 | 1 | 4.5 |  | 120 | 540 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12PX2XN |  | 12'12'12' | 36' PX2XN | 1 |  | Produce | 46.26 | 26 | Off Cycle | 115 | 1.2 | 4.5 |  | 144 | 540 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'8PX2XN |  | 8'8'8'8'8' | 40' PX2XN | 1 |  | Produce | 51.4 | 26 | Off Cycle | 115 | 1 | 5 |  | 120 | 600 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12PX2XN |  | 8'8'12'12' | 40' PX2XN | 1 |  | Produce | 51.4 | 26 | Off Cycle | 115 | 1.2 | 5 |  | 144 | 600 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'12PX2XN |  | 8'8'8'8'12' | 44' PX2XN | 1 |  | Produce | 56.54 | 26 | Off Cycle | 115 | 1.2 | 5.5 |  | 144 | 660 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12PX2XN |  | 8'12'12'12' | 44' PX2XN | 1 |  | Produce | 56.54 | 26 | Off Cycle | 115 | 1.4 | 5.5 |  | 168 | 660 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12PX2XN |  | 8'8'8'12'12' | 48' PX2XN | 1 |  | Produce | 61.68 | 26 | Off Cycle | 115 | 1.4 | 6 |  | 168 | 720 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12PX2XN |  | 12'12'12'12' | 48' PX2XN | 1 |  | Produce | 61.68 | 26 | Off Cycle | 115 | 1.6 | 6 |  | 192 | 720 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12PX2XN/FT4R |  | 8'12'/4' | 24' PX2XN/FT4R | 1 |  | Produce/ Floral | 29.48 | 26 | Off Cycle | 115 | 0.9 | 2.8 | 0 | 108 | 336 | 0 |  |  | SORIT 12 |  |  | 7/8
|  | SX2LP 3D MEAT, SEAFOOD | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4SX2LP |  | 4' | 4' SX2LP | 1 |  | 3D Meat/ Seafood | 3.912 | 26 | Off Cycle | 115 | 0.1 | 0.75 |  | 12 | 90 | 0 |  |  | SORIT 12
6SX2LP |  | 6' | 6' SX2LP | 1 |  | 3D Meat/ Seafood | 5.868 | 26 | Off Cycle | 115 | 0.2 | 1.35 |  | 24 | 162 | 0 |  |  | SORIT 12
8SX2LP |  | 8' | 8' SX2LP | 1 |  | 3D Meat/ Seafood | 7.824 | 26 | Off Cycle | 115 | 0.2 | 1.5 |  | 24 | 180 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12SX2LP |  | 12' | 12' SX2LP | 1 |  | 3D Meat/ Seafood | 11.736 | 26 | Off Cycle | 115 | 0.4 | 2.3 |  | 48 | 276 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8SX2LP |  | 8'8' | 16' SX2LP | 1 |  | 3D Meat/ Seafood | 15.648 | 26 | Off Cycle | 115 | 0.4 | 3 | 0 | 48 | 360 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12SX2LP |  | 8'12' | 20' SX2LP | 1 |  | 3D Meat/ Seafood | 19.56 | 26 | Off Cycle | 115 | 0.6 | 3.8 | 0 | 72 | 456 | 0 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8SX2LP |  | 8'8'8' | 24' SX2LP | 1 |  | 3D Meat/ Seafood | 23.472 | 26 | Off Cycle | 115 | 0.6 | 4.5 | 0 | 72 | 540 | 0 |  |  | SORIT 12 |  |  | 7/8 | 5/8
12'12SX2LP |  | 12'12' | 24' SX2LP | 1 |  | 3D Meat/ Seafood | 23.472 | 26 | Off Cycle | 115 | 0.8 | 4.6 | 0 | 96 | 552 | 0 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'12SX2LP |  | 8'8'12' | 28' SX2LP | 1 |  | 3D Meat/ Seafood | 27.384 | 26 | Off Cycle | 115 | 0.8 | 5.3 | 0 | 96 | 636 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8SX2LP |  | 8'8'8'8' | 32' SX2LP | 1 |  | 3D Meat/ Seafood | 31.296 | 26 | Off Cycle | 115 | 0.8 | 6 | 0 | 96 | 720 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'12'12SX2LP |  | 8'12'12' | 32' SX2LP | 1 |  | 3D Meat/ Seafood | 31.296 | 26 | Off Cycle | 115 | 1 | 6.1 | 0 | 120 | 732 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'12SX2LP |  | 8'8'8'12' | 36' SX2LP | 1 |  | 3D Meat/ Seafood | 35.208 | 26 | Off Cycle | 115 | 1 | 6.8 | 0 | 120 | 816 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12'12SX2LP |  | 12'12'12' | 36' SX2LP | 1 |  | 3D Meat/ Seafood | 35.208 | 26 | Off Cycle | 115 | 1.2 | 6.9 | 0 | 144 | 828 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8'8SX2LP |  | 8'8'8'8'8' | 40' SX2LP | 1 |  | 3D Meat/ Seafood | 39.12 | 26 | Off Cycle | 115 | 1 | 7.5 | 0 | 120 | 900 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12SX2LP |  | 8'8'12'12' | 40' SX2LP | 1 |  | 3D Meat/ Seafood | 39.12 | 26 | Off Cycle | 115 | 1.2 | 7.6 | 0 | 144 | 912 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'12SX2LP |  | 8'8'8'8'12' | 44' SX2LP | 1 |  | 3D Meat/ Seafood | 43.032 | 26 | Off Cycle | 115 | 1.2 | 8.3 | 0 | 144 | 996 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12SX2LP |  | 8'12'12'12' | 44' SX2LP | 1 |  | 3D Meat/ Seafood | 43.032 | 26 | Off Cycle | 115 | 1.4 | 8.4 | 0 | 168 | 1008 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12SX2LP |  | 8'8'8'12'12' | 48' SX2LP | 1 |  | 3D Meat/ Seafood | 46.944 | 26 | Off Cycle | 115 | 1.4 | 9.1 | 0 | 168 | 1092 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12SX2LP |  | 12'12'12'12' | 48' SX2LP | 1 |  | 3D Meat/ Seafood | 46.944 | 26 | Off Cycle | 115 | 1.6 | 9.2 | 0 | 192 | 1104 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12SX2LP |  | 8'8'12'12'12' | 52' SX2LP | 1 |  | 3D Meat/ Seafood | 50.856 | 26 | Off Cycle | 115 | 1.6 | 9.9 | 0 | 192 | 1188 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12SX2LP |  | 8'12'12'12'12 | 56' SX2LP | 1 |  | 3D Meat/ Seafood | 54.768 | 26 | Off Cycle | 115 | 1.8 | 10.7 | 0 | 216 | 1284 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'6SX2LP |  | 8'8'8'8'6' | 38' SX2LP | 1 |  | 3D Meat Island | 37.164 | 26 | Off Cycle | 115 | 1 | 7.35 | 0 | 120 | 882 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | QFGCEI-A | FROZEN FOOD | [8 empty] | LED | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEI-A |  | 2 | QFGCEI-A | 1 |  | Frozen Food | 2.672 | -11 | HG 2 Wire | 115 | 0.5 | 0.48 | 3.63 | 60 | 57.6 | 435.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEI-A |  | 3 | QFGCEI-A | 1 |  | Frozen Food | 4.008 | -11 | HG 2 Wire | 115 | 0.75 | 0.73 | 5.62 | 90 | 87.6 | 674.4 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEI-A |  | 4 | QFGCEI-A | 1 |  | Frozen Food | 5.344 | -11 | HG 2 Wire | 115 | 1 | 0.98 | 7.42 | 120 | 117.6 | 890.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEI-A |  | 5 | QFGCEI-A | 1 |  | Frozen Food | 6.68 | -11 | HG 2 Wire | 115 | 1.25 | 1.2 | 9.15 | 150 | 144 | 1098 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEI-A |  | 3,3 | 6Dr QFGCEI-A | 1 |  | Frozen Food | 8.016 | -11 | HG 2 Wire | 115 | 1.5 | 1.46 | 11.24 | 180 | 175.2 | 1348.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEI-A |  | 4,3 | 7Dr QFGCEI-A | 1 |  | Frozen Food | 9.352 | -11 | HG 2 Wire | 115 | 1.75 | 1.71 | 13.04 | 210 | 205.2 | 1564.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEI-A |  | 4,4 | 8Dr QFGCEI-A | 1 |  | Frozen Food | 10.688 | -11 | HG 2 Wire | 115 | 2 | 1.96 | 14.84 | 240 | 235.2 | 1780.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEI-A |  | 5,3 | 8Dr QFGCEI-A | 1 |  | Frozen Food | 10.688 | -11 | HG 2 Wire | 115 | 2 | 1.93 | 14.77 | 240 | 231.6 | 1772.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEI-A |  | 5,4 | 9Dr QFGCEI-A | 1 |  | Frozen Food | 12.024 | -11 | HG 2 Wire | 115 | 2.25 | 2.18 | 16.57 | 270 | 261.6 | 1988.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEI-A |  | 3,3,3 | 9Dr QFGCEI-A | 1 |  | Frozen Food | 12.024 | -11 | HG 2 Wire | 115 | 2.25 | 2.19 | 16.86 | 270 | 262.8 | 2023.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEI-A |  | 5,5 | 10Dr QFGCEI-A | 1 |  | Frozen Food | 13.36 | -11 | HG 2 Wire | 115 | 2.5 | 2.4 | 18.3 | 300 | 288 | 2196 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QFGCEI-A |  | 4,3,3 | 10Dr QFGCEI-A | 1 |  | Frozen Food | 13.36 | -11 | HG 2 Wire | 115 | 2.5 | 2.44 | 18.66 | 300 | 292.8 | 2239.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QFGCEI-A |  | 5,3,3 | 11Dr QFGCEI-A | 1 |  | Frozen Food | 14.696 | -11 | HG 2 Wire | 115 | 2.75 | 2.66 | 20.39 | 330 | 319.2 | 2446.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3QFGCEI-A |  | 4,4,3 | 11Dr QFGCEI-A | 1 |  | Frozen Food | 14.696 | -11 | HG 2 Wire | 115 | 2.75 | 2.69 | 20.46 | 330 | 322.8 | 2455.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4QFGCEI-A |  | 4,4,4 | 12Dr QFGCEI-A | 1 |  | Frozen Food | 16.032 | -11 | HG 2 Wire | 115 | 3 | 2.94 | 22.26 | 360 | 352.8 | 2671.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3QFGCEI-A |  | 5,4,3 | 12Dr QFGCEI-A | 1 |  | Frozen Food | 16.032 | -11 | HG 2 Wire | 115 | 3 | 2.91 | 22.19 | 360 | 349.2 | 2662.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4QFGCEI-A |  | 5,4,4 | 13Dr QFGCEI-A | 1 |  | Frozen Food | 17.368 | -11 | HG 2 Wire | 115 | 3.25 | 3.16 | 23.99 | 390 | 379.2 | 2878.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QFGCEI-A |  | 5,5,3 | 13Dr QFGCEI-A | 1 |  | Frozen Food | 17.368 | -11 | HG 2 Wire | 115 | 3.25 | 3.13 | 23.92 | 390 | 375.6 | 2870.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QFGCEI-A |  | 5,5,4 | 14Dr QFGCEI-A | 1 |  | Frozen Food | 18.704 | -11 | HG 2 Wire | 115 | 3.5 | 3.38 | 25.72 | 420 | 405.6 | 3086.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEI-A |  | 4,4,3,3 | 14Dr QFGCEI-A | 1 |  | Frozen Food | 18.704 | -11 | HG 2 Wire | 115 | 3.5 | 3.42 | 26.08 | 420 | 410.4 | 3129.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QFGCEI-A |  | 5,5,5 | 15Dr QFGCEI-A | 1 |  | Frozen Food | 20.04 | -11 | HG 2 Wire | 115 | 3.75 | 3.6 | 27.45 | 450 | 432 | 3294 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEI-A |  | 4,4,4,3 | 15Dr QFGCEI-A | 1 |  | Frozen Food | 20.04 | -11 | HG 2 Wire | 115 | 3.75 | 3.67 | 27.88 | 450 | 440.4 | 3345.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEI-A |  | 5,5,3,3 | 16Dr QFGCEI-A | 1 |  | Frozen Food | 21.376 | -11 | HG 2 Wire | 115 | 4 | 3.86 | 29.54 | 480 | 463.2 | 3544.8 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEI-A |  | 4,4,4,4 | 16Dr QFGCEI-A | 1 |  | Frozen Food | 21.376 | -11 | HG 2 Wire | 115 | 4 | 3.92 | 29.68 | 480 | 470.4 | 3561.6 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,3,2QFGCEI-A |  | 4,3,2 | 9Dr QFGCEI-A | 1 |  | Frozen Food | 12.024 | -11 | HG 2 Wire | 115 | 2.25 | 2.19 | 16.67 | 270 | 262.8 | 2000.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEI-A |  | 5,3,2 | 10Dr QFGCEI-A | 1 |  | Frozen Food | 13.36 | -11 | HG 2 Wire | 115 | 2.5 | 2.41 | 18.4 | 300 | 289.2 | 2208 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEI-A |  | 5,3,3,3 | 14Dr QFGCEI-A | 1 |  | Frozen Food | 18.704 | -11 | HG 2 Wire | 115 | 3.5 | 3.39 | 26.01 | 420 | 406.8 | 3121.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEI-A |  | 4,4,3,2 | 13Dr QFGCEI-A | 1 |  | Frozen Food | 17.368 | -11 | HG 2 Wire | 115 | 3.25 | 3.17 | 24.09 | 390 | 380.4 | 2890.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QFGCEI-A | ICE CREAM | [8 empty] | LED | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEI-AIC |  | 2 | QFGCEI-A | 1 |  | Ice Cream | 2.776 | -18 | HG 2 Wire | 115 | 0.5 | 0.48 | 3.63 | 60 | 57.6 | 435.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEI-AIC |  | 3 | QFGCEI-A | 1 |  | Ice Cream | 4.164 | -18 | HG 2 Wire | 115 | 0.75 | 0.73 | 5.62 | 90 | 87.6 | 674.4 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEI-AIC |  | 4 | QFGCEI-A | 1 |  | Ice Cream | 5.552 | -18 | HG 2 Wire | 115 | 1 | 0.98 | 7.42 | 120 | 117.6 | 890.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEI-AIC |  | 5 | QFGCEI-A | 1 |  | Ice Cream | 6.94 | -18 | HG 2 Wire | 115 | 1.25 | 1.2 | 9.15 | 150 | 144 | 1098 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEI-AIC |  | 3,3 | 6Dr QFGCEI-A | 1 |  | Ice Cream | 8.328 | -18 | HG 2 Wire | 115 | 1.5 | 1.46 | 11.24 | 180 | 175.2 | 1348.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEI-AIC |  | 4,3 | 7Dr QFGCEI-A | 1 |  | Ice Cream | 9.716 | -18 | HG 2 Wire | 115 | 1.75 | 1.71 | 13.04 | 210 | 205.2 | 1564.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEI-AIC |  | 4,4 | 8Dr QFGCEI-A | 1 |  | Ice Cream | 11.104 | -18 | HG 2 Wire | 115 | 2 | 1.96 | 14.84 | 240 | 235.2 | 1780.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEI-AIC |  | 5,3 | 8Dr QFGCEI-A | 1 |  | Ice Cream | 11.104 | -18 | HG 2 Wire | 115 | 2 | 1.93 | 14.77 | 240 | 231.6 | 1772.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEI-AIC |  | 5,4 | 9Dr QFGCEI-A | 1 |  | Ice Cream | 12.492 | -18 | HG 2 Wire | 115 | 2.25 | 2.18 | 16.57 | 270 | 261.6 | 1988.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEI-AIC |  | 3,3,3 | 9Dr QFGCEI-A | 1 |  | Ice Cream | 12.492 | -18 | HG 2 Wire | 115 | 2.25 | 2.19 | 16.86 | 270 | 262.8 | 2023.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEI-AIC |  | 5,5 | 10Dr QFGCEI-A | 1 |  | Ice Cream | 13.88 | -18 | HG 2 Wire | 115 | 2.5 | 2.4 | 18.3 | 300 | 288 | 2196 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,3,3QFGCEI-AIC |  | 4,3,3 | 10Dr QFGCEI-A | 1 |  | Ice Cream | 13.88 | -18 | HG 2 Wire | 115 | 2.5 | 2.44 | 18.66 | 300 | 292.8 | 2239.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3,3QFGCEI-AIC |  | 5,3,3 | 11Dr QFGCEI-A | 1 |  | Ice Cream | 15.268 | -18 | HG 2 Wire | 115 | 2.75 | 2.66 | 20.39 | 330 | 319.2 | 2446.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3QFGCEI-AIC |  | 4,4,3 | 11Dr QFGCEI-A | 1 |  | Ice Cream | 15.268 | -18 | HG 2 Wire | 115 | 2.75 | 2.69 | 20.46 | 330 | 322.8 | 2455.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4QFGCEI-AIC |  | 4,4,4 | 12Dr QFGCEI-A | 1 |  | Ice Cream | 16.656 | -18 | HG 2 Wire | 115 | 3 | 2.94 | 22.26 | 360 | 352.8 | 2671.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3QFGCEI-AIC |  | 5,4,3 | 12Dr QFGCEI-A | 1 |  | Ice Cream | 16.656 | -18 | HG 2 Wire | 115 | 3 | 2.91 | 22.19 | 360 | 349.2 | 2662.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4QFGCEI-AIC |  | 5,4,4 | 13Dr QFGCEI-A | 1 |  | Ice Cream | 18.044 | -18 | HG 2 Wire | 115 | 3.25 | 3.16 | 23.99 | 390 | 379.2 | 2878.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QFGCEI-AIC |  | 5,5,3 | 13Dr QFGCEI-A | 1 |  | Ice Cream | 18.044 | -18 | HG 2 Wire | 115 | 3.25 | 3.13 | 23.92 | 390 | 375.6 | 2870.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QFGCEI-AIC |  | 5,5,4 | 14Dr QFGCEI-A | 1 |  | Ice Cream | 19.432 | -18 | HG 2 Wire | 115 | 3.5 | 3.38 | 25.72 | 420 | 405.6 | 3086.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEI-AIC |  | 4,4,3,3 | 14Dr QFGCEI-A | 1 |  | Ice Cream | 19.432 | -18 | HG 2 Wire | 115 | 3.5 | 3.42 | 26.08 | 420 | 410.4 | 3129.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QFGCEI-AIC |  | 5,5,5 | 15Dr QFGCEI-A | 1 |  | Ice Cream | 20.82 | -18 | HG 2 Wire | 115 | 3.75 | 3.6 | 27.45 | 450 | 432 | 3294 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEI-AIC |  | 4,4,4,3 | 15Dr QFGCEI-A | 1 |  | Ice Cream | 20.82 | -18 | HG 2 Wire | 115 | 3.75 | 3.67 | 27.88 | 450 | 440.4 | 3345.6 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEI-AIC |  | 5,5,3,3 | 16Dr QFGCEI-A | 1 |  | Ice Cream | 22.208 | -18 | HG 2 Wire | 115 | 4 | 3.86 | 29.54 | 480 | 463.2 | 3544.8 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEI-AIC |  | 4,4,4,4 | 16Dr QFGCEI-A | 1 |  | Ice Cream | 22.208 | -18 | HG 2 Wire | 115 | 4 | 3.92 | 29.68 | 480 | 470.4 | 3561.6 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,3,2QFGCEI-AIC |  | 4,3,2 | 9Dr QFGCEI-A | 1 |  | Ice Cream | 12.492 | -18 | HG 2 Wire | 115 | 2.25 | 2.19 | 16.67 | 270 | 262.8 | 2000.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEI-AIC |  | 5,3,2 | 10Dr QFGCEI-A | 1 |  | Ice Cream | 13.88 | -18 | HG 2 Wire | 115 | 2.5 | 2.41 | 18.4 | 300 | 289.2 | 2208 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEI-AIC |  | 5,3,3,3 | 14Dr QFGCEI-A | 1 |  | Ice Cream | 19.432 | -18 | HG 2 Wire | 115 | 3.5 | 3.39 | 26.01 | 420 | 406.8 | 3121.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEI-AIC |  | 4,4,3,2 | 13Dr QFGCEI-A | 1 |  | Ice Cream | 18.044 | -18 | HG 2 Wire | 115 | 3.25 | 3.17 | 24.09 | 390 | 380.4 | 2890.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QFGCEID-A | FROZEN FOOD BACK TO BACK | [8 empty] | LED | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEID-A |  | 2 | QFGCEID-A | 1 |  | Frozen Food | 2.392 | -11 | HG 2 Wire | 115 | 0.5 | 0.48 | 3.63 | 60 | 57.6 | 435.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEID-A |  | 3 | QFGCEID-A | 1 |  | Frozen Food | 3.588 | -11 | HG 2 Wire | 115 | 0.75 | 0.73 | 5.25 | 90 | 87.6 | 630 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEID-A |  | 4 | QFGCEID-A | 1 |  | Frozen Food | 4.784 | -11 | HG 2 Wire | 115 | 1 | 0.98 | 7.02 | 120 | 117.6 | 842.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEID-A |  | 5 | QFGCEID-A | 1 |  | Frozen Food | 5.98 | -11 | HG 2 Wire | 115 | 1.25 | 1.2 | 8.61 | 150 | 144 | 1033.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEID-A |  | 3,3 | 6Dr QFGCEID-A | 1 |  | Frozen Food | 7.176 | -11 | HG 2 Wire | 115 | 1.5 | 1.46 | 10.5 | 180 | 175.2 | 1260 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEID-A |  | 4,3 | 7Dr QFGCEID-A | 1 |  | Frozen Food | 8.372 | -11 | HG 2 Wire | 115 | 1.75 | 1.71 | 12.27 | 210 | 205.2 | 1472.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEID-A |  | 4,4 | 8Dr QFGCEID-A | 1 |  | Frozen Food | 9.568 | -11 | HG 2 Wire | 115 | 2 | 1.96 | 14.04 | 240 | 235.2 | 1684.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEID-A |  | 5,3 | 8Dr QFGCEID-A | 1 |  | Frozen Food | 9.568 | -11 | HG 2 Wire | 115 | 2 | 1.93 | 13.86 | 240 | 231.6 | 1663.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEID-A |  | 5,4 | 9Dr QFGCEID-A | 1 |  | Frozen Food | 10.764 | -11 | HG 2 Wire | 115 | 2.25 | 2.18 | 15.63 | 270 | 261.6 | 1875.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEID-A |  | 3,3,3 | 9Dr QFGCEID-A | 1 |  | Frozen Food | 10.764 | -11 | HG 2 Wire | 115 | 2.25 | 2.19 | 15.75 | 270 | 262.8 | 1890 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEID-A |  | 5,5 | 10Dr QFGCEID-A | 1 |  | Frozen Food | 11.96 | -11 | HG 2 Wire | 115 | 2.5 | 2.4 | 17.22 | 300 | 288 | 2066.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QFGCEID-A |  | 4,3,3 | 10Dr QFGCEID-A | 1 |  | Frozen Food | 11.96 | -11 | HG 2 Wire | 115 | 2.5 | 2.44 | 17.52 | 300 | 292.8 | 2102.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QFGCEID-A |  | 5,3,3 | 11Dr QFGCEID-A | 1 |  | Frozen Food | 13.156 | -11 | HG 2 Wire | 115 | 2.75 | 2.66 | 19.11 | 330 | 319.2 | 2293.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,3QFGCEID-A |  | 4,4,3 | 11Dr QFGCEID-A | 1 |  | Frozen Food | 13.156 | -11 | HG 2 Wire | 115 | 2.75 | 2.69 | 19.29 | 330 | 322.8 | 2314.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,4QFGCEID-A |  | 4,4,4 | 12Dr QFGCEID-A | 1 |  | Frozen Food | 14.352 | -11 | HG 2 Wire | 115 | 3 | 2.94 | 21.06 | 360 | 352.8 | 2527.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,3QFGCEID-A |  | 5,4,3 | 12Dr QFGCEID-A | 1 |  | Frozen Food | 14.352 | -11 | HG 2 Wire | 115 | 3 | 2.91 | 20.88 | 360 | 349.2 | 2505.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,4QFGCEID-A |  | 5,4,4 | 13Dr QFGCEID-A | 1 |  | Frozen Food | 15.548 | -11 | HG 2 Wire | 115 | 3.25 | 3.16 | 22.65 | 390 | 379.2 | 2718 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5,3QFGCEID-A |  | 5,5,3 | 13Dr QFGCEID-A | 1 |  | Frozen Food | 15.548 | -11 | HG 2 Wire | 115 | 3.25 | 3.13 | 22.47 | 390 | 375.6 | 2696.4 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5,4QFGCEID-A |  | 5,5,4 | 14Dr QFGCEID-A | 1 |  | Frozen Food | 16.744 | -11 | HG 2 Wire | 115 | 3.5 | 3.38 | 24.24 | 420 | 405.6 | 2908.8 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEID-A |  | 4,4,3,3 | 14Dr QFGCEID-A | 1 |  | Frozen Food | 16.744 | -11 | HG 2 Wire | 115 | 3.5 | 3.42 | 24.54 | 420 | 410.4 | 2944.8 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5,5QFGCEID-A |  | 5,5,5 | 15Dr QFGCEID-A | 1 |  | Frozen Food | 17.94 | -11 | HG 2 Wire | 115 | 3.75 | 3.6 | 25.83 | 450 | 432 | 3099.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEID-A |  | 4,4,4,3 | 15Dr QFGCEID-A | 1 |  | Frozen Food | 17.94 | -11 | HG 2 Wire | 115 | 3.75 | 3.67 | 26.31 | 450 | 440.4 | 3157.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEID-A |  | 5,5,3,3 | 16Dr QFGCEID-A | 1 |  | Frozen Food | 19.136 | -11 | HG 2 Wire | 115 | 4 | 3.86 | 27.72 | 480 | 463.2 | 3326.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEID-A |  | 4,4,4,4 | 16Dr QFGCEID-A | 1 |  | Frozen Food | 19.136 | -11 | HG 2 Wire | 115 | 4 | 3.92 | 28.08 | 480 | 470.4 | 3369.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,2QFGCEID-A |  | 4,3,2 | 9Dr QFGCEID-A | 1 |  | Frozen Food | 10.764 | -11 | HG 2 Wire | 115 | 2.25 | 2.19 | 15.9 | 270 | 262.8 | 1908 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEID-A |  | 5,3,2 | 10Dr QFGCEID-A | 1 |  | Frozen Food | 11.96 | -11 | HG 2 Wire | 115 | 2.5 | 2.41 | 17.49 | 300 | 289.2 | 2098.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEID-A |  | 5,3,3,3 | 14Dr QFGCEID-A | 1 |  | Frozen Food | 16.744 | -11 | HG 2 Wire | 115 | 3.5 | 3.39 | 24.36 | 420 | 406.8 | 2923.2 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEID-A |  | 4,4,3,2 | 13Dr QFGCEID-A | 1 |  | Frozen Food | 15.548 | -11 | HG 2 Wire | 115 | 3.25 | 3.17 | 22.92 | 390 | 380.4 | 2750.4 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
|  | QFGCEID-A | ICE CREAM BACK TO BACK | [8 empty] | LED | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEID-AIC |  | 2 | QFGCEID-A | 1 |  | Ice Cream | 2.484 | -18 | HG 2 Wire | 115 | 0.5 | 0.48 | 3.63 | 60 | 57.6 | 435.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEID-AIC |  | 3 | QFGCEID-A | 1 |  | Ice Cream | 3.726 | -18 | HG 2 Wire | 115 | 0.75 | 0.73 | 5.25 | 90 | 87.6 | 630 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEID-AIC |  | 4 | QFGCEID-A | 1 |  | Ice Cream | 4.968 | -18 | HG 2 Wire | 115 | 1 | 0.98 | 7.02 | 120 | 117.6 | 842.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEID-AIC |  | 5 | QFGCEID-A | 1 |  | Ice Cream | 6.21 | -18 | HG 2 Wire | 115 | 1.25 | 1.2 | 8.61 | 150 | 144 | 1033.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEID-AIC |  | 3,3 | 6Dr QFGCEID-A | 1 |  | Ice Cream | 7.452 | -18 | HG 2 Wire | 115 | 1.5 | 1.46 | 10.5 | 180 | 175.2 | 1260 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEID-AIC |  | 4,3 | 7Dr QFGCEID-A | 1 |  | Ice Cream | 8.694 | -18 | HG 2 Wire | 115 | 1.75 | 1.71 | 12.27 | 210 | 205.2 | 1472.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEID-AIC |  | 4,4 | 8Dr QFGCEID-A | 1 |  | Ice Cream | 9.936 | -18 | HG 2 Wire | 115 | 2 | 1.96 | 14.04 | 240 | 235.2 | 1684.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEID-AIC |  | 5,3 | 8Dr QFGCEID-A | 1 |  | Ice Cream | 9.936 | -18 | HG 2 Wire | 115 | 2 | 1.93 | 13.86 | 240 | 231.6 | 1663.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEID-AIC |  | 5,4 | 9Dr QFGCEID-A | 1 |  | Ice Cream | 11.178 | -18 | HG 2 Wire | 115 | 2.25 | 2.18 | 15.63 | 270 | 261.6 | 1875.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEID-AIC |  | 3,3,3 | 9Dr QFGCEID-A | 1 |  | Ice Cream | 11.178 | -18 | HG 2 Wire | 115 | 2.25 | 2.19 | 15.75 | 270 | 262.8 | 1890 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEID-AIC |  | 5,5 | 10Dr QFGCEID-A | 1 |  | Ice Cream | 12.42 | -18 | HG 2 Wire | 115 | 2.5 | 2.4 | 17.22 | 300 | 288 | 2066.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QFGCEID-AIC |  | 4,3,3 | 10Dr QFGCEID-A | 1 |  | Ice Cream | 12.42 | -18 | HG 2 Wire | 115 | 2.5 | 2.44 | 17.52 | 300 | 292.8 | 2102.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QFGCEID-AIC |  | 5,3,3 | 11Dr QFGCEID-A | 1 |  | Ice Cream | 13.662 | -18 | HG 2 Wire | 115 | 2.75 | 2.66 | 19.11 | 330 | 319.2 | 2293.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,3QFGCEID-AIC |  | 4,4,3 | 11Dr QFGCEID-A | 1 |  | Ice Cream | 13.662 | -18 | HG 2 Wire | 115 | 2.75 | 2.69 | 19.29 | 330 | 322.8 | 2314.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,4QFGCEID-AIC |  | 4,4,4 | 12Dr QFGCEID-A | 1 |  | Ice Cream | 14.904 | -18 | HG 2 Wire | 115 | 3 | 2.94 | 21.06 | 360 | 352.8 | 2527.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,3QFGCEID-AIC |  | 5,4,3 | 12Dr QFGCEID-A | 1 |  | Ice Cream | 14.904 | -18 | HG 2 Wire | 115 | 3 | 2.91 | 20.88 | 360 | 349.2 | 2505.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,4QFGCEID-AIC |  | 5,4,4 | 13Dr QFGCEID-A | 1 |  | Ice Cream | 16.146 | -18 | HG 2 Wire | 115 | 3.25 | 3.16 | 22.65 | 390 | 379.2 | 2718 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QFGCEID-AIC |  | 5,5,3 | 13Dr QFGCEID-A | 1 |  | Ice Cream | 16.146 | -18 | HG 2 Wire | 115 | 3.25 | 3.13 | 22.47 | 390 | 375.6 | 2696.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QFGCEID-AIC |  | 5,5,4 | 14Dr QFGCEID-A | 1 |  | Ice Cream | 17.388 | -18 | HG 2 Wire | 115 | 3.5 | 3.38 | 24.24 | 420 | 405.6 | 2908.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEID-AIC |  | 4,4,3,3 | 14Dr QFGCEID-A | 1 |  | Ice Cream | 17.388 | -18 | HG 2 Wire | 115 | 3.5 | 3.42 | 24.54 | 420 | 410.4 | 2944.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QFGCEID-AIC |  | 5,5,5 | 15Dr QFGCEID-A | 1 |  | Ice Cream | 18.63 | -18 | HG 2 Wire | 115 | 3.75 | 3.6 | 25.83 | 450 | 432 | 3099.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEID-AIC |  | 4,4,4,3 | 15Dr QFGCEID-A | 1 |  | Ice Cream | 18.63 | -18 | HG 2 Wire | 115 | 3.75 | 3.67 | 26.31 | 450 | 440.4 | 3157.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEID-AIC |  | 5,5,3,3 | 16Dr QFGCEID-A | 1 |  | Ice Cream | 19.872 | -18 | HG 2 Wire | 115 | 4 | 3.86 | 27.72 | 480 | 463.2 | 3326.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEID-AIC |  | 4,4,4,4 | 16Dr QFGCEID-A | 1 |  | Ice Cream | 19.872 | -18 | HG 2 Wire | 115 | 4 | 3.92 | 28.08 | 480 | 470.4 | 3369.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,2QFGCEID-AIC |  | 4,3,2 | 9Dr QFGCEID-A | 1 |  | Ice Cream | 11.178 | -18 | HG 2 Wire | 115 | 2.25 | 2.19 | 15.9 | 270 | 262.8 | 1908 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEID-AIC |  | 5,3,2 | 10Dr QFGCEID-A | 1 |  | Ice Cream | 12.42 | -18 | HG 2 Wire | 115 | 2.5 | 2.41 | 17.49 | 300 | 289.2 | 2098.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEID-AIC |  | 5,3,3,3 | 14Dr QFGCEID-A | 1 |  | Ice Cream | 17.388 | -18 | HG 2 Wire | 115 | 3.5 | 3.39 | 24.36 | 420 | 406.8 | 2923.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEID-AIC |  | 4,4,3,2 | 13Dr QFGCEID-A | 1 |  | Ice Cream | 16.146 | -18 | HG 2 Wire | 115 | 3.25 | 3.17 | 22.92 | 390 | 380.4 | 2750.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QIL MEAT PROMO'S | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
6QIL |  | 6' | QIL |  |  | Dual Temp Promo | 2.25 | -17 | HG 2 Wire | 115 | 0.64 | 0 | 0.78 | 76.8 | 0 | 93.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 5/8
8QIL |  | 8' | QIL |  |  | Dual Temp Promo | 3 | -17 | HG 2 Wire | 115 | 0.64 | 0 | 0.98 | 76.8 | 0 | 117.6 | E14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
12QIL |  | 12' | QIL |  |  | Dual Temp Promo | 4.5 | -17 | HG 2 Wire | 115 | 0.96 | 0 | 1.46 | 115.2 | 0 | 175.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8QIL |  | 8'8' | 16' QIL |  |  | Dual Temp Promo | 6 | -17 | HG 2 Wire | 115 | 1.28 | 0 | 1.96 | 153.6 | 0 | 235.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
|  | QLV5V-A | FROZEN FOOD WITH LED LIGHTS | [8 empty] | LED | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QLV5V-A |  | 2 | QLV5V-A | 1 |  | Frozen Food | 2.65 | -11 | HG 2 Wire | 115 | 0.5 | 0.48 | 3.83 | 60 | 57.6 | 459.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QLV5V-A |  | 3 | QLV5V-A | 1 |  | Frozen Food | 3.975 | -11 | HG 2 Wire | 115 | 0.75 | 0.73 | 5.62 | 90 | 87.6 | 674.4 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QLV5V-A |  | 4 | QLV5V-A | 1 |  | Frozen Food | 5.3 | -11 | HG 2 Wire | 115 | 1 | 0.98 | 7.42 | 120 | 117.6 | 890.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QLV5V-A |  | 5 | QLV5V-A | 1 |  | Frozen Food | 6.625 | -11 | HG 2 Wire | 115 | 1.25 | 1.2 | 9.15 | 150 | 144 | 1098 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QLV5V-A |  | 3,3 | 6Dr QLV5V-A | 1 |  | Frozen Food | 7.95 | -11 | HG 2 Wire | 115 | 1.5 | 1.46 | 11.24 | 180 | 175.2 | 1348.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QLV5V-A |  | 4,3 | 7Dr QLV5V-A | 1 |  | Frozen Food | 9.275 | -11 | HG 2 Wire | 115 | 1.75 | 1.71 | 13.04 | 210 | 205.2 | 1564.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QLV5V-A |  | 4,4 | 8Dr QLV5V-A | 1 |  | Frozen Food | 10.6 | -11 | HG 2 Wire | 115 | 2 | 1.96 | 14.84 | 240 | 235.2 | 1780.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QLV5V-A |  | 5,3 | 8Dr QLV5V-A | 1 |  | Frozen Food | 10.6 | -11 | HG 2 Wire | 115 | 2 | 1.93 | 14.77 | 240 | 231.6 | 1772.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QLV5V-A |  | 5,4 | 9Dr QLV5V-A | 1 |  | Frozen Food | 11.925 | -11 | HG 2 Wire | 115 | 2.25 | 2.18 | 16.57 | 270 | 261.6 | 1988.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QLV5V-A |  | 3,3,3 | 9Dr QLV5V-A | 1 |  | Frozen Food | 11.925 | -11 | HG 2 Wire | 115 | 2.25 | 2.19 | 16.86 | 270 | 262.8 | 2023.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QLV5V-A |  | 5,5 | 10Dr QLV5V-A | 1 |  | Frozen Food | 13.25 | -11 | HG 2 Wire | 115 | 2.5 | 2.4 | 18.3 | 300 | 288 | 2196 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QLV5V-A |  | 4,3,3 | 10Dr QLV5V-A | 1 |  | Frozen Food | 13.25 | -11 | HG 2 Wire | 115 | 2.5 | 2.44 | 18.66 | 300 | 292.8 | 2239.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QLV5V-A |  | 5,3,3 | 11Dr QLV5V-A | 1 |  | Frozen Food | 14.575 | -11 | HG 2 Wire | 115 | 2.75 | 2.66 | 20.39 | 330 | 319.2 | 2446.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3QLV5V-A |  | 4,4,3 | 11Dr QLV5V-A | 1 |  | Frozen Food | 14.575 | -11 | HG 2 Wire | 115 | 2.75 | 2.69 | 20.46 | 330 | 322.8 | 2455.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4QLV5V-A |  | 4,4,4 | 12Dr QLV5V-A | 1 |  | Frozen Food | 15.9 | -11 | HG 2 Wire | 115 | 3 | 2.94 | 22.26 | 360 | 352.8 | 2671.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3QLV5V-A |  | 5,4,3 | 12Dr QLV5V-A | 1 |  | Frozen Food | 15.9 | -11 | HG 2 Wire | 115 | 3 | 2.91 | 22.19 | 360 | 349.2 | 2662.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4QLV5V-A |  | 5,4,4 | 13Dr QLV5V-A | 1 |  | Frozen Food | 17.225 | -11 | HG 2 Wire | 115 | 3.25 | 3.16 | 23.99 | 390 | 379.2 | 2878.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QLV5V-A |  | 5,5,3 | 13Dr QLV5V-A | 1 |  | Frozen Food | 17.225 | -11 | HG 2 Wire | 115 | 3.25 | 3.13 | 23.92 | 390 | 375.6 | 2870.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QLV5V-A |  | 5,5,4 | 14Dr QLV5V-A | 1 |  | Frozen Food | 18.55 | -11 | HG 2 Wire | 115 | 3.5 | 3.38 | 25.72 | 420 | 405.6 | 3086.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QLV5V-A |  | 4,4,3,3 | 14Dr QLV5V-A | 1 |  | Frozen Food | 18.55 | -11 | HG 2 Wire | 115 | 3.5 | 3.42 | 26.08 | 420 | 410.4 | 3129.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QLV5V-A |  | 5,5,5 | 15Dr QLV5V-A | 1 |  | Frozen Food | 19.875 | -11 | HG 2 Wire | 115 | 3.75 | 3.6 | 27.45 | 450 | 432 | 3294 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QLV5V-A |  | 4,4,4,3 | 15Dr QLV5V-A | 1 |  | Frozen Food | 19.875 | -11 | HG 2 Wire | 115 | 3.75 | 3.67 | 27.88 | 450 | 440.4 | 3345.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QLV5V-A |  | 5,5,3,3 | 16Dr QLV5V-A | 1 |  | Frozen Food | 21.2 | -11 | HG 2 Wire | 115 | 4 | 3.86 | 29.54 | 480 | 463.2 | 3544.8 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4QLV5V-A |  | 4,4,4,4 | 16Dr QLV5V-A | 1 |  | Frozen Food | 21.2 | -11 | HG 2 Wire | 115 | 4 | 3.92 | 29.68 | 480 | 470.4 | 3561.6 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,3,2QLV5V-A |  | 4,3,2 | 9Dr QLV5V-A | 1 |  | Frozen Food | 11.925 | -11 | HG 2 Wire | 115 | 2.25 | 2.19 | 16.87 | 270 | 262.8 | 2024.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QLV5V-A |  | 5,3,2 | 10Dr QLV5V-A | 1 |  | Frozen Food | 13.25 | -11 | HG 2 Wire | 115 | 2.5 | 2.41 | 18.6 | 300 | 289.2 | 2232 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 39637
5,3,3,3QLV5V-A |  | 5,3,3,3 | 14Dr QLV5V-A | 1 |  | Frozen Food | 18.55 | -11 | HG 2 Wire | 115 | 3.5 | 3.39 | 26.01 | 420 | 406.8 | 3121.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QLV5V-A |  | 4,4,3,2 | 13Dr QLV5V-A | 1 |  | Frozen Food | 17.225 | -11 | HG 2 Wire | 115 | 3.25 | 3.17 | 24.29 | 390 | 380.4 | 2914.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QIV5V-A | ICE CREAM WITH LED LIGHTS | [8 empty] | LED | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QIV5V-A |  | 2 | QIV5V-A | 1 |  | Ice Cream | 2.852 | -18 | HG 2 Wire | 115 | 0.5 | 0.48 | 3.83 | 60 | 57.6 | 459.6 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3QIV5V-A |  | 3 | QIV5V-A | 1 |  | Ice Cream | 4.278 | -18 | HG 2 Wire | 115 | 0.75 | 0.73 | 5.62 | 90 | 87.6 | 674.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4QIV5V-A |  | 4 | QIV5V-A | 1 |  | Ice Cream | 5.704 | -18 | HG 2 Wire | 115 | 1 | 0.98 | 7.42 | 120 | 117.6 | 890.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QIV5V-A |  | 5 | QIV5V-A | 1 |  | Ice Cream | 7.13 | -18 | HG 2 Wire | 115 | 1.25 | 1.2 | 9.15 | 150 | 144 | 1098 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QIV5V-A |  | 3,3 | 6Dr QIV5V-A | 1 |  | Ice Cream | 8.556 | -18 | HG 2 Wire | 115 | 1.5 | 1.46 | 11.24 | 180 | 175.2 | 1348.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3QIV5V-A |  | 4,3 | 7Dr QIV5V-A | 1 |  | Ice Cream | 9.982 | -18 | HG 2 Wire | 115 | 1.75 | 1.71 | 13.04 | 210 | 205.2 | 1564.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4QIV5V-A |  | 4,4 | 8Dr QIV5V-A | 1 |  | Ice Cream | 11.408 | -18 | HG 2 Wire | 115 | 2 | 1.96 | 14.84 | 240 | 235.2 | 1780.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QIV5V-A |  | 5,3 | 8Dr QIV5V-A | 1 |  | Ice Cream | 11.408 | -18 | HG 2 Wire | 115 | 2 | 1.93 | 14.77 | 240 | 231.6 | 1772.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QIV5V-A |  | 5,4 | 9Dr QIV5V-A | 1 |  | Ice Cream | 12.834 | -18 | HG 2 Wire | 115 | 2.25 | 2.18 | 16.57 | 270 | 261.6 | 1988.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
3,3,3QIV5V-A |  | 3,3,3 | 9Dr QIV5V-A | 1 |  | Ice Cream | 12.834 | -18 | HG 2 Wire | 115 | 2.25 | 2.19 | 16.86 | 270 | 262.8 | 2023.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5QIV5V-A |  | 5,5 | 10Dr QIV5V-A | 1 |  | Ice Cream | 14.26 | -18 | HG 2 Wire | 115 | 2.5 | 2.4 | 18.3 | 300 | 288 | 2196 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3QIV5V-A |  | 4,3,3 | 10Dr QIV5V-A | 1 |  | Ice Cream | 14.26 | -18 | HG 2 Wire | 115 | 2.5 | 2.44 | 18.66 | 300 | 292.8 | 2239.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3QIV5V-A |  | 5,3,3 | 11Dr QIV5V-A | 1 |  | Ice Cream | 15.686 | -18 | HG 2 Wire | 115 | 2.75 | 2.66 | 20.39 | 330 | 319.2 | 2446.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3QIV5V-A |  | 4,4,3 | 11Dr QIV5V-A | 1 |  | Ice Cream | 15.686 | -18 | HG 2 Wire | 115 | 2.75 | 2.69 | 20.46 | 330 | 322.8 | 2455.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4QIV5V-A |  | 4,4,4 | 12Dr QIV5V-A | 1 |  | Ice Cream | 17.112 | -18 | HG 2 Wire | 115 | 3 | 2.94 | 22.26 | 360 | 352.8 | 2671.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3QIV5V-A |  | 5,4,3 | 12Dr QIV5V-A | 1 |  | Ice Cream | 17.112 | -18 | HG 2 Wire | 115 | 3 | 2.91 | 22.19 | 360 | 349.2 | 2662.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4QIV5V-A |  | 5,4,4 | 13Dr QIV5V-A | 1 |  | Ice Cream | 18.538 | -18 | HG 2 Wire | 115 | 3.25 | 3.16 | 23.99 | 390 | 379.2 | 2878.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QIV5V-A |  | 5,5,3 | 13Dr QIV5V-A | 1 |  | Ice Cream | 18.538 | -18 | HG 2 Wire | 115 | 3.25 | 3.13 | 23.92 | 390 | 375.6 | 2870.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QIV5V-A |  | 5,5,4 | 14Dr QIV5V-A | 1 |  | Ice Cream | 19.964 | -18 | HG 2 Wire | 115 | 3.5 | 3.38 | 25.72 | 420 | 405.6 | 3086.4 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,3QIV5V-A |  | 4,4,3,3 | 14Dr QIV5V-A | 1 |  | Ice Cream | 19.964 | -18 | HG 2 Wire | 115 | 3.5 | 3.42 | 26.08 | 420 | 410.4 | 3129.6 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,5QIV5V-A |  | 5,5,5 | 15Dr QIV5V-A | 1 |  | Ice Cream | 21.39 | -18 | HG 2 Wire | 115 | 3.75 | 3.6 | 27.45 | 450 | 432 | 3294 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3QIV5V-A |  | 4,4,4,3 | 15Dr QIV5V-A | 1 |  | Ice Cream | 21.39 | -18 | HG 2 Wire | 115 | 3.75 | 3.67 | 27.88 | 450 | 440.4 | 3345.6 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3QIV5V-A |  | 5,5,3,3 | 16Dr QIV5V-A | 1 |  | Ice Cream | 22.816 | -18 | HG 2 Wire | 115 | 4 | 3.86 | 29.54 | 480 | 463.2 | 3544.8 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4QIV5V-A |  | 4,4,4,4 | 16Dr QIV5V-A | 1 |  | Ice Cream | 22.816 | -18 | HG 2 Wire | 115 | 4 | 3.92 | 29.68 | 480 | 470.4 | 3561.6 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,2QIV5V-A |  | 4,4,3,2 | 13Dr QIV5V-A | 1 |  | Ice Cream | 18.538 | -18 | HG 2 Wire | 115 | 3.25 | 3.17 | 24.29 | 390 | 380.4 | 2914.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QHZVP PRODUCE |  | Also applies to QHZVP3/QHZVP1 | [13 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QHZVP |  | 4' | 4' QHZVP | 1 |  | Produce | 5.08 | 26 | Off Cycle | 115 | 0.25 | 0.5 |  | 30 | 60 | 0 |  |  | SORIT 12 |  |  | 1/2
6QHZVP |  | 6' | 6' QHZVP | 1 |  | Produce | 7.62 | 26 | Off Cycle | 115 | 0.4 | 0.8 |  | 48 | 96 | 0 |  |  | SORIT 12 |  |  | 5/8
8QHZVP |  | 8' | 8' QHZVP | 1 |  | Produce | 10.16 | 26 | Off Cycle | 115 | 0.5 | 1 |  | 60 | 120 | 0 |  |  | SORIT 12 |  |  | 1/2
12QHZVP |  | 12' | 12' QHZVP | 1 |  | Produce | 15.24 | 26 | Off Cycle | 115 | 0.75 | 1.5 |  | 90 | 180 | 0 |  |  | SORIT 12 |  |  | 5/8
8'8QHZVP |  | 8'8' | 16' QHZVP | 1 |  | Produce | 20.32 | 26 | Off Cycle | 115 | 1 | 2 |  | 120 | 240 | 0 |  |  | SORIT 12 |  |  | 5/8
8'12QHZVP |  | 8'12' | 20' QHZVP | 1 |  | Produce | 25.4 | 26 | Off Cycle | 115 | 1.25 | 2.5 |  | 150 | 300 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'8QHZVP |  | 8'8'8' | 24' QHZVP | 1 |  | Produce | 30.48 | 26 | Off Cycle | 115 | 1.5 | 3 |  | 180 | 360 | 0 |  |  | SORIT 12 |  |  | 7/8
12'12QHZVP |  | 12'12' | 24' QHZVP | 1 |  | Produce | 30.48 | 26 | Off Cycle | 115 | 1.5 | 3 |  | 180 | 360 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'12QHZVP |  | 8'8'12' | 28' QHZVP | 1 |  | Produce | 35.56 | 26 | Off Cycle | 115 | 1.75 | 3.5 |  | 210 | 420 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'8'8QHZVP |  | 8'8'8'8' | 32' QHZVP | 1 |  | Produce | 40.64 | 26 | Off Cycle | 115 | 2 | 4 |  | 240 | 480 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'12'12QHZVP |  | 8'12'12' | 32' QHZVP | 1 |  | Produce | 40.64 | 26 | Off Cycle | 115 | 2 | 4 |  | 240 | 480 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8'12QHZVP |  | 8'8'8'12' | 36' QHZVP | 1 |  | Produce | 45.72 | 26 | Off Cycle | 115 | 2.25 | 4.5 |  | 270 | 540 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12QHZVP |  | 12'12'12' | 36' QHZVP | 1 |  | Produce | 45.72 | 26 | Off Cycle | 115 | 2.25 | 4.5 |  | 270 | 540 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'8QHZVP |  | 8'8'8'8'8' | 40' QHZVP | 1 |  | Produce | 50.8 | 26 | Off Cycle | 115 | 2.5 | 5 |  | 300 | 600 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12QHZVP |  | 8'8'12'12' | 40' QHZVP | 1 |  | Produce | 50.8 | 26 | Off Cycle | 115 | 2.5 | 5 |  | 300 | 600 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'12QHZVP |  | 8'8'8'8'12' | 44' QHZVP | 1 |  | Produce | 55.88 | 26 | Off Cycle | 115 | 2.75 | 5.5 |  | 330 | 660 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12QHZVP |  | 8'12'12'12' | 44' QHZVP | 1 |  | Produce | 55.88 | 26 | Off Cycle | 115 | 2.75 | 5.5 |  | 330 | 660 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12QHZVP |  | 8'8'8'12'12' | 48' QHZVP | 1 |  | Produce | 60.96 | 26 | Off Cycle | 115 | 3 | 6 |  | 360 | 720 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12QHZVP |  | 12'12'12'12' | 48' QHZVP | 1 |  | Produce | 60.96 | 26 | Off Cycle | 115 | 3 | 6 |  | 360 | 720 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | QM4AL MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QM4AL |  | 4' | 4'QM4AL | 1 |  | MD Fresh Meat | 5.6 | 23 | Off Cycle | 115 | 0.52 | 1.5 | 0 | 62.4 | 180 | 0 |  |  | SORIT 12
6QM4AL |  | 6' | 6'QM4AL | 1 |  | MD Fresh Meat | 8.4 | 23 | Off Cycle | 115 | 0.7 | 2.56 | 0 | 84 | 307.2 | 0 |  |  | SORIT 12
8QM4AL |  | 8' | 8'QM4AL | 1 |  | MD Fresh Meat | 11.2 | 23 | Off Cycle | 115 | 1.04 | 3 | 0 | 124.8 | 360 | 0 |  |  | SORIT 12 |  |  | 7/8
12QM4AL |  | 12' | 12'QM4AL | 1 |  | MD Fresh Meat | 16.8 | 23 | Off Cycle | 115 | 1.56 | 5.5 | 0 | 187.2 | 660 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8QM4AL |  | 8'8' | 16' QM4AL | 1 |  | MD Fresh Meat | 22.4 | 23 | Off Cycle | 115 | 2.08 | 6 | 0 | 249.6 | 720 | 0 |  |  | SORIT 12 |  |  | 1 1/8
8'12QM4AL |  | 8'12' | 20' QM4AL | 1 |  | MD Fresh Meat | 28 | 23 | Off Cycle | 115 | 2.6 | 8.5 | 0 | 312 | 1020 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8QM4AL |  | 8'8'8' | 24' QM4AL | 1 |  | MD Fresh Meat | 33.6 | 23 | Off Cycle | 115 | 3.12 | 9 | 0 | 374.4 | 1080 | 0 |  |  | SORIT 15 |  |  | 1 3/8
12'12QM4AL |  | 12'12' | 24' QM4AL | 1 |  | MD Fresh Meat | 33.6 | 23 | Off Cycle | 115 | 3.12 | 11 | 0 | 374.4 | 1320 | 0 |  |  | SORIT 15 |  |  | 1 3/8
8'8'12QM4AL |  | 8'8'12' | 28' QM4AL | 1 |  | MD Fresh Meat | 39.2 | 23 | Off Cycle | 115 | 3.64 | 11.5 | 0 | 436.8 | 1380 | 0 |  |  | SORIT 20 |  |  | 1 3/8
8'8'8'8QM4AL |  | 8'8'8'8' | 32' QM4AL | 1 |  | MD Fresh Meat | 44.8 | 23 | Off Cycle | 115 | 4.16 | 12 | 0 | 499.2 | 1440 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12QM4AL |  | 8'12'12' | 32' QM4AL | 1 |  | MD Fresh Meat | 44.8 | 23 | Off Cycle | 115 | 4.16 | 14 | 0 | 499.2 | 1680 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12QM4AL |  | 8'8'8'12' | 36' QM4AL | 1 |  | MD Fresh Meat | 50.4 | 23 | Off Cycle | 115 | 4.68 | 14.5 | 0 | 561.6 | 1740 | 0 |  |  | SORIT 20 |  |  | 1 5/8
12'12'12QM4AL |  | 12'12'12' | 36' QM4AL | 1 |  | MD Fresh Meat | 50.4 | 23 | Off Cycle | 115 | 4.68 | 16.5 | 0 | 561.6 | 1980 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'8QM4AL |  | 8'8'8'8'8' | 40' QM4AL | 1 |  | MD Fresh Meat | 56 | 23 | Off Cycle | 115 | 5.2 | 15 | 0 | 624 | 1800 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'12'12QM4AL |  | 8'8'12'12' | 40' QM4AL | 1 |  | MD Fresh Meat | 56 | 23 | Off Cycle | 115 | 5.2 | 17 | 0 | 624 | 2040 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'12QM4AL |  | 8'8'8'8'12' | 44' QM4AL | 1 |  | MD Fresh Meat | 61.6 | 23 | Off Cycle | 115 | 5.72 | 17.5 | 0 | 686.4 | 2100 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12'12QM4AL |  | 8'12'12'12' | 44' QM4AL | 1 |  | MD Fresh Meat | 61.6 | 23 | Off Cycle | 115 | 5.72 | 19.5 | 0 | 686.4 | 2340 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12'12QM4AL |  | 8'8'8'12'12' | 48' QM4AL | 1 |  | MD Fresh Meat | 67.2 | 23 | Off Cycle | 115 | 6.24 | 20 | 0 | 748.8 | 2400 | 0 |  |  | SORIT 20 |  |  | 2 1/8
12'12'12'12QM4AL |  | 12'12'12'12' | 48' QM4AL | 1 |  | MD Fresh Meat | 67.2 | 23 | Off Cycle | 115 | 6.24 | 22 | 0 | 748.8 | 2640 | 0 |  |  | SORIT 20 |  |  | 2 1/8
|  | QM4AG MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QM4AG |  | 4' | 4'QM4AG | 1 |  | MD Fresh Meat | 4.64 | 24 | Off Cycle | 115 | 0.52 | 1.25 | 0 | 62.4 | 150 | 0 |  |  | SORIT 12
6QM4AG |  | 6' | 6'QM4AG | 1 |  | MD Fresh Meat | 6.96 | 24 | Off Cycle | 115 | 0.7 | 2 | 0 | 84 | 240 | 0 |  |  | SORIT 12
8QM4AG |  | 8' | 8'QM4AG | 1 |  | MD Fresh Meat | 9.28 | 24 | Off Cycle | 115 | 1.04 | 2.5 | 0 | 124.8 | 300 | 0 |  |  | SORIT 12 |  |  | 7/8
12QM4AG |  | 12' | 12'QM4AG | 1 |  | MD Fresh Meat | 13.92 | 24 | Off Cycle | 115 | 1.56 | 3.75 | 0 | 187.2 | 450 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8QM4AG |  | 8'8' | 16' QM4AG | 1 |  | MD Fresh Meat | 18.56 | 24 | Off Cycle | 115 | 2.08 | 5 | 0 | 249.6 | 600 | 0 |  |  | SORIT 12 |  |  | 1 1/8
8'12QM4AG |  | 8'12' | 20' QM4AG | 1 |  | MD Fresh Meat | 23.2 | 24 | Off Cycle | 115 | 2.6 | 6.25 | 0 | 312 | 750 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8QM4AG |  | 8'8'8' | 24' QM4AG | 1 |  | MD Fresh Meat | 27.84 | 24 | Off Cycle | 115 | 3.12 | 7.5 | 0 | 374.4 | 900 | 0 |  |  | SORIT 15 |  |  | 1 3/8
12'12QM4AG |  | 12'12' | 24' QM4AG | 1 |  | MD Fresh Meat | 27.84 | 24 | Off Cycle | 115 | 3.12 | 7.5 | 0 | 374.4 | 900 | 0 |  |  | SORIT 15 |  |  | 1 3/8
8'8'12QM4AG |  | 8'8'12' | 28' QM4AG | 1 |  | MD Fresh Meat | 32.48 | 24 | Off Cycle | 115 | 3.64 | 8.75 | 0 | 436.8 | 1050 | 0 |  |  | SORIT 20 |  |  | 1 3/8
8'8'8'8QM4AG |  | 8'8'8'8' | 32' QM4AG | 1 |  | MD Fresh Meat | 37.12 | 24 | Off Cycle | 115 | 4.16 | 10 | 0 | 499.2 | 1200 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12QM4AG |  | 8'12'12' | 32' QM4AG | 1 |  | MD Fresh Meat | 37.12 | 24 | Off Cycle | 115 | 4.16 | 10 | 0 | 499.2 | 1200 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12QM4AG |  | 8'8'8'12' | 36' QM4AG | 1 |  | MD Fresh Meat | 41.76 | 24 | Off Cycle | 115 | 4.68 | 11.25 | 0 | 561.6 | 1350 | 0 |  |  | SORIT 20 |  |  | 1 5/8
12'12'12QM4AG |  | 12'12'12' | 36' QM4AG | 1 |  | MD Fresh Meat | 41.76 | 24 | Off Cycle | 115 | 4.68 | 11.25 | 0 | 561.6 | 1350 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'8QM4AG |  | 8'8'8'8'8' | 40' QM4AG | 1 |  | MD Fresh Meat | 46.4 | 24 | Off Cycle | 115 | 5.2 | 12.5 | 0 | 624 | 1500 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'12'12QM4AG |  | 8'8'12'12' | 40' QM4AG | 1 |  | MD Fresh Meat | 46.4 | 24 | Off Cycle | 115 | 5.2 | 12.5 | 0 | 624 | 1500 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'12QM4AG |  | 8'8'8'8'12' | 44' QM4AG | 1 |  | MD Fresh Meat | 51.04 | 24 | Off Cycle | 115 | 5.72 | 13.75 | 0 | 686.4 | 1650 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12'12QM4AG |  | 8'12'12'12' | 44' QM4AG | 1 |  | MD Fresh Meat | 51.04 | 24 | Off Cycle | 115 | 5.72 | 13.75 | 0 | 686.4 | 1650 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12'12QM4AG |  | 8'8'8'12'12' | 48' QM4AG | 1 |  | MD Fresh Meat | 55.68 | 24 | Off Cycle | 115 | 6.24 | 15 | 0 | 748.8 | 1800 | 0 |  |  | SORIT 20 |  |  | 2 1/8
12'12'12'12QM4AG |  | 12'12'12'12' | 48' QM4AG | 1 |  | MD Fresh Meat | 55.68 | 24 | Off Cycle | 115 | 6.24 | 15 | 0 | 748.8 | 1800 | 0 |  |  | SORIT 20 |  |  | 2 1/8
|  | QM2AG - AG1 - AG3 MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
6QM2AG |  | 6' | 6'QM2AG | 1 |  | 2D Fresh Meat | 5.61 | 24 | Off Cycle | 115 | 0.4 | 1.3 | 0 | 48 | 156 | 0
8QM2AG |  | 8' | 8'QM2AG | 1 |  | 2D Fresh Meat | 7.48 | 24 | Off Cycle | 115 | 0.4 | 1.5 | 0 | 48 | 180 | 0 |  |  | SORIT 12 |  |  | 7/8
12QM2AG |  | 12' | 12'QM2AG | 1 |  | 2D Fresh Meat | 11.22 | 24 | Off Cycle | 115 | 0.6 | 2.25 | 0 | 72 | 270 | 0 |  |  | SORIT 12 |  |  | 7/8
6'8QM2AG |  | 6'8' | 14' QM2AG | 1 |  | 2D Fresh Meat | 13.09 | 24 | Off Cycle | 115 | 0.8 | 2.8 | 0 | 96 | 336 | 0
8'8QM2AG |  | 8'8' | 16' QM2AG | 1 |  | 2D Fresh Meat | 14.96 | 24 | Off Cycle | 115 | 0.8 | 3 | 0 | 96 | 360 | 0 |  |  | SORIT 12 |  |  | 1 1/8
8'12QM2AG |  | 8'12' | 20' QM2AG | 1 |  | 2D Fresh Meat | 18.7 | 24 | Off Cycle | 115 | 1 | 3.75 | 0 | 120 | 450 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8QM2AG |  | 8'8'8' | 24' QM2AG | 1 |  | 2D Fresh Meat | 22.44 | 24 | Off Cycle | 115 | 1.2 | 4.5 | 0 | 144 | 540 | 0 |  |  | SORIT 15 |  |  | 1 3/8
12'12QM2AG |  | 12'12' | 24' QM2AG | 1 |  | 2D Fresh Meat | 22.44 | 24 | Off Cycle | 115 | 1.2 | 4.5 | 0 | 144 | 540 | 0 |  |  | SORIT 15 |  |  | 1 3/8
8'8'12QM2AG |  | 8'8'12' | 28' QM2AG | 1 |  | 2D Fresh Meat | 26.18 | 24 | Off Cycle | 115 | 1.4 | 5.25 | 0 | 168 | 630 | 0 |  |  | SORIT 20 |  |  | 1 3/8
8'8'8'8QM2AG |  | 8'8'8'8' | 32' QM2AG | 1 |  | 2D Fresh Meat | 29.92 | 24 | Off Cycle | 115 | 1.6 | 6 | 0 | 192 | 720 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12QM2AG |  | 8'12'12' | 32' QM2AG | 1 |  | 2D Fresh Meat | 29.92 | 24 | Off Cycle | 115 | 1.6 | 6 | 0 | 192 | 720 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12QM2AG |  | 8'8'8'12' | 36' QM2AG | 1 |  | 2D Fresh Meat | 33.66 | 24 | Off Cycle | 115 | 1.8 | 6.75 | 0 | 216 | 810 | 0 |  |  | SORIT 20 |  |  | 1 5/8
12'12'12QM2AG |  | 12'12'12' | 36' QM2AG | 1 |  | 2D Fresh Meat | 33.66 | 24 | Off Cycle | 115 | 1.8 | 6.75 | 0 | 216 | 810 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'8QM2AG |  | 8'8'8'8'8' | 40' QM2AG | 1 |  | 2D Fresh Meat | 37.4 | 24 | Off Cycle | 115 | 2 | 7.5 | 0 | 240 | 900 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'12'12QM2AG |  | 8'8'12'12' | 40' QM2AG | 1 |  | 2D Fresh Meat | 37.4 | 24 | Off Cycle | 115 | 2 | 7.5 | 0 | 240 | 900 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'12QM2AG |  | 8'8'8'8'12' | 44' QM2AG | 1 |  | 2D Fresh Meat | 41.14 | 24 | Off Cycle | 115 | 2.2 | 8.25 | 0 | 264 | 990 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12'12QM2AG |  | 8'12'12'12' | 44' QM2AG | 1 |  | 2D Fresh Meat | 41.14 | 24 | Off Cycle | 115 | 2.2 | 8.25 | 0 | 264 | 990 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12'12QM2AG |  | 8'8'8'12'12' | 48' QM2AG | 1 |  | 2D Fresh Meat | 44.88 | 24 | Off Cycle | 115 | 2.4 | 9 | 0 | 288 | 1080 | 0 |  |  | SORIT 20 |  |  | 2 1/8
12'12'12'12QM2AG |  | 12'12'12'12' | 48' QM2AG | 1 |  | 2D Fresh Meat | 44.88 | 24 | Off Cycle | 115 | 2.4 | 9 | 0 | 288 | 1080 | 0 |  |  | SORIT 20 |  |  | 2 1/8
|  | QM1A FRESH MEAT |  | Also applies to QM1A1 & QM1A3 | [13 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QM1A |  | 4' | 4'QM1A | 1 |  | Fresh Meat | 2 | 24 | Off Cycle | 115 | 0.2 | 0 | 0.06 | 24 | 0 | 7.2
6QM1A |  | 6' | 6'QM1A | 1 |  | Fresh Meat | 3 | 24 | Off Cycle | 115 | 0.4 | 0 | 0.08 | 48 | 0 | 9.6
8QM1A1 |  | 8' | 8'QM1A | 1 |  | Fresh Meat | 4 | 24 | Off Cycle | 115 | 0.4 | 0 | 0.12 | 48 | 0 | 14.4 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12QM1A |  | 12' | 12'QM1A | 1 |  | Fresh Meat | 6 | 24 | Off Cycle | 115 | 0.6 | 0 | 0.18 | 72 | 0 | 21.6 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8QM1A |  | 8'8' | 16' QM1A | 1 |  | Fresh Meat | 8 | 24 | Off Cycle | 115 | 0.8 | 0 | 0.24 | 96 | 0 | 28.8 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12QM1A |  | 8'12' | 20'QM1A | 1 |  | Fresh Meat | 10 | 24 | Off Cycle | 115 | 1 | 0 | 0.3 | 120 | 0 | 36 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8QM1A |  | 8'8'8' | 24' QM1A | 1 |  | Fresh Meat | 12 | 24 | Off Cycle | 115 | 1.2 | 0 | 0.36 | 144 | 0 | 43.2 |  |  | SORIT 12 |  |  | 7/8 | 5/8
12'12QM1A |  | 12'12' | 24' QM1A | 1 |  | Fresh Meat | 12 | 24 | Off Cycle | 115 | 1.2 | 0 | 0.36 | 144 | 0 | 43.2 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'12QM1A |  | 8'8'12' | 28' QM1A | 1 |  | Fresh Meat | 14 | 24 | Off Cycle | 115 | 1.4 | 0 | 0.42 | 168 | 0 | 50.4 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'8QM1A |  | 8'8'8'8' | 32' QM1A | 1 |  | Fresh Meat | 16 | 24 | Off Cycle | 115 | 1.6 | 0 | 0.48 | 192 | 0 | 57.6 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'12'12QM1A |  | 8'12'12' | 32' QM1A | 1 |  | Fresh Meat | 16 | 24 | Off Cycle | 115 | 1.6 | 0 | 0.48 | 192 | 0 | 57.6 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'12QM1A |  | 8'8'8'12' | 36' QM1A | 1 |  | Fresh Meat | 18 | 24 | Off Cycle | 115 | 1.8 | 0 | 0.54 | 216 | 0 | 64.8 |  |  | SORIT 12 |  |  | 7/8 | 5/8
12'12'12QM1A |  | 12'12'12' | 36' QM1A | 1 |  | Fresh Meat | 18 | 24 | Off Cycle | 115 | 1.8 | 0 | 0.54 | 216 | 0 | 64.8 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'8'8QM1A |  | 8'8'8'8'8' | 40' QM1A | 1 |  | Fresh Meat | 20 | 24 | Off Cycle | 115 | 2 | 0 | 0.6 | 240 | 0 | 72 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'12'12QM1A |  | 8'8'12'12' | 40' QM1A | 1 |  | Fresh Meat | 20 | 24 | Off Cycle | 115 | 2 | 0 | 0.6 | 240 | 0 | 72 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8'8'12QM1A |  | 8'8'8'8'12' | 44' QM1A | 1 |  | Fresh Meat | 22 | 24 | Off Cycle | 115 | 2.2 | 0 | 0.66 | 264 | 0 | 79.2 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'12'12'12QM1A |  | 8'12'12'12' | 44' QM1A | 1 |  | Fresh Meat | 22 | 24 | Off Cycle | 115 | 2.2 | 0 | 0.66 | 264 | 0 | 79.2 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8'12'12QM1A |  | 8'8'8'12'12' | 48' QM1A | 1 |  | Fresh Meat | 24 | 24 | Off Cycle | 115 | 2.4 | 0 | 0.72 | 288 | 0 | 86.4 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12'12QM1A |  | 12'12'12'12' | 48' QM1A | 1 |  | Fresh Meat | 24 | 24 | Off Cycle | 115 | 2.4 | 0 | 0.72 | 288 | 0 | 86.4 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12'12QM1A |  | 8'8'12'12'12' | 52' QM1A | 1 |  | Fresh Meat | 26 | 24 | Off Cycle | 115 | 2.6 | 0 | 0.78 | 312 | 0 | 93.6 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'12'12'12'12QM1A |  | 8'12'12'12'12 | 56' QM1A | 1 |  | Fresh Meat | 28 | 24 | Off Cycle | 115 | 2.8 | 0 | 0.84 | 336 | 0 | 100.8 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | QM1AG FRESH MEAT NEW CASES | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QM1AG |  | 4' | 4'QM1AG | 1 |  | Fresh Meat | 1.92 | 24 | Off Cycle | 115 | 0.2 | 0 | 0.06 | 24 | 0 | 7.2
6QM1AG |  | 6' | 6'QM1AG | 1 |  | Fresh Meat | 2.88 | 24 | Off Cycle | 115 | 0.4 | 0 | 0.08 | 48 | 0 | 9.6
8QM1A1G |  | 8' | 8'QM1AG | 1 |  | Fresh Meat | 3.84 | 24 | Off Cycle | 115 | 0.4 | 0 | 0.12 | 48 | 0 | 14.4 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12QM1AG |  | 12' | 12'QM1AG | 1 |  | Fresh Meat | 5.76 | 24 | Off Cycle | 115 | 0.6 | 0 | 0.18 | 72 | 0 | 21.6 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8QM1AG |  | 8'8' | 16' QM1AG | 1 |  | Fresh Meat | 7.68 | 24 | Off Cycle | 115 | 0.8 | 0 | 0.24 | 96 | 0 | 28.8 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12QM1AG |  | 8'12' | 20'QM1AG | 1 |  | Fresh Meat | 9.6 | 24 | Off Cycle | 115 | 1 | 0 | 0.3 | 120 | 0 | 36 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8QM1AG |  | 8'8'8' | 24' QM1AG | 1 |  | Fresh Meat | 11.52 | 24 | Off Cycle | 115 | 1.2 | 0 | 0.36 | 144 | 0 | 43.2 |  |  | SORIT 12 |  |  | 7/8 | 5/8
12'12QM1AG |  | 12'12' | 24' QM1AG | 1 |  | Fresh Meat | 11.52 | 24 | Off Cycle | 115 | 1.2 | 0 | 0.36 | 144 | 0 | 43.2 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'12QM1AG |  | 8'8'12' | 28' QM1AG | 1 |  | Fresh Meat | 13.44 | 24 | Off Cycle | 115 | 1.4 | 0 | 0.42 | 168 | 0 | 50.4 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'8QM1AG |  | 8'8'8'8' | 32' QM1AG | 1 |  | Fresh Meat | 15.36 | 24 | Off Cycle | 115 | 1.6 | 0 | 0.48 | 192 | 0 | 57.6 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'12'12QM1AG |  | 8'12'12' | 32' QM1AG | 1 |  | Fresh Meat | 15.36 | 24 | Off Cycle | 115 | 1.6 | 0 | 0.48 | 192 | 0 | 57.6 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'12QM1AG |  | 8'8'8'12' | 36' QM1AG | 1 |  | Fresh Meat | 17.28 | 24 | Off Cycle | 115 | 1.8 | 0 | 0.54 | 216 | 0 | 64.8 |  |  | SORIT 12 |  |  | 7/8 | 5/8
12'12'12QM1AG |  | 12'12'12' | 36' QM1AG | 1 |  | Fresh Meat | 17.28 | 24 | Off Cycle | 115 | 1.8 | 0 | 0.54 | 216 | 0 | 64.8 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'8'8QM1AG |  | 8'8'8'8'8' | 40' QM1AG | 1 |  | Fresh Meat | 19.2 | 24 | Off Cycle | 115 | 2 | 0 | 0.6 | 240 | 0 | 72 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'12'12QM1AG |  | 8'8'12'12' | 40' QM1AG | 1 |  | Fresh Meat | 19.2 | 24 | Off Cycle | 115 | 2 | 0 | 0.6 | 240 | 0 | 72 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8'8'12QM1AG |  | 8'8'8'8'12' | 44' QM1AG | 1 |  | Fresh Meat | 21.12 | 24 | Off Cycle | 115 | 2.2 | 0 | 0.66 | 264 | 0 | 79.2 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'12'12'12QM1AG |  | 8'12'12'12' | 44' QM1AG | 1 |  | Fresh Meat | 21.12 | 24 | Off Cycle | 115 | 2.2 | 0 | 0.66 | 264 | 0 | 79.2 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8'12'12QM1AG |  | 8'8'8'12'12' | 48' QM1AG | 1 |  | Fresh Meat | 23.04 | 24 | Off Cycle | 115 | 2.4 | 0 | 0.72 | 288 | 0 | 86.4 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12'12QM1AG |  | 12'12'12'12' | 48' QM1AG | 1 |  | Fresh Meat | 23.04 | 24 | Off Cycle | 115 | 2.4 | 0 | 0.72 | 288 | 0 | 86.4 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12'12QM1AG |  | 8'8'12'12'12' | 52' QM1AG | 1 |  | Fresh Meat | 24.96 | 24 | Off Cycle | 115 | 2.6 | 0 | 0.78 | 312 | 0 | 93.6 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'12'12'12'12QM1AG |  | 8'12'12'12'12 | 56' QM1AG | 1 |  | Fresh Meat | 26.88 | 24 | Off Cycle | 115 | 2.8 | 0 | 0.84 | 336 | 0 | 100.8 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | QM5 MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QM5 |  | 4' | 4'QM5 | 1 |  | MD Fresh Meat | 5.58 | 23 | Off Cycle | 115 | 0.25 | 1.75 | 0 | 30 | 210 | 0
6QM5 |  | 6' | 6'QM5 | 1 |  | MD Fresh Meat | 8.37 | 23 | Off Cycle | 115 | 0.4 | 3 | 0 | 48 | 360 | 0
8QM5 |  | 8' | 8'QM5 | 1 |  | MD Fresh Meat | 11.16 | 23 | Off Cycle | 115 | 0.5 | 3.5 | 0 | 60 | 420 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12QM5 |  | 12' | 12'QM5 | 1 |  | MD Fresh Meat | 16.74 | 23 | Off Cycle | 115 | 0.75 | 5.25 | 0 | 90 | 630 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8QM5 |  | 8'8' | 16' QM5 | 1 |  | MD Fresh Meat | 22.32 | 23 | Off Cycle | 115 | 1 | 7 | 0 | 120 | 840 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12QM5 |  | 8'12' | 20' QM5 | 1 |  | MD Fresh Meat | 27.9 | 23 | Off Cycle | 115 | 1.25 | 8.75 | 0 | 150 | 1050 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8QM5 |  | 8'8'8' | 24' QM5 | 1 |  | MD Fresh Meat | 33.48 | 23 | Off Cycle | 115 | 1.5 | 10.5 | 0 | 180 | 1260 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12QM5 |  | 12'12' | 24' QM5 | 1 |  | MD Fresh Meat | 33.48 | 23 | Off Cycle | 115 | 1.5 | 10.5 | 0 | 180 | 1260 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'12QM5 |  | 8'8'12' | 28' QM5 | 1 |  | MD Fresh Meat | 39.06 | 23 | Off Cycle | 115 | 1.75 | 12.25 | 0 | 210 | 1470 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8QM5 |  | 8'8'8'8' | 32' QM5 | 1 |  | MD Fresh Meat | 44.64 | 23 | Off Cycle | 115 | 2 | 14 | 0 | 240 | 1680 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'12'12QM5 |  | 8'12'12' | 32' QM5 | 1 |  | MD Fresh Meat | 44.64 | 23 | Off Cycle | 115 | 2 | 14 | 0 | 240 | 1680 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'12QM5 |  | 8'8'8'12' | 36' QM5 | 1 |  | MD Fresh Meat | 50.22 | 23 | Off Cycle | 115 | 2.25 | 15.75 | 0 | 270 | 1890 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
12'12'12QM5 |  | 12'12'12' | 36' QM5 | 1 |  | MD Fresh Meat | 50.22 | 23 | Off Cycle | 115 | 2.25 | 15.75 | 0 | 270 | 1890 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'8'8QM5 |  | 8'8'8'8'8' | 40' QM5 | 1 |  | MD Fresh Meat | 55.8 | 23 | Off Cycle | 115 | 2.5 | 17.5 | 0 | 300 | 2100 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12QM5 |  | 8'8'12'12' | 40' QM5 | 1 |  | MD Fresh Meat | 55.8 | 23 | Off Cycle | 115 | 2.5 | 17.5 | 0 | 300 | 2100 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12QM5 |  | 8'8'8'8'12' | 44' QM5 | 1 |  | MD Fresh Meat | 61.38 | 23 | Off Cycle | 115 | 2.75 | 19.25 | 0 | 330 | 2310 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12QM5 |  | 8'12'12'12' | 44' QM5 | 1 |  | MD Fresh Meat | 61.38 | 23 | Off Cycle | 115 | 2.75 | 19.25 | 0 | 330 | 2310 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12QM5 |  | 8'8'8'12'12' | 48' QM5 | 1 |  | MD Fresh Meat | 66.96 | 23 | Off Cycle | 115 | 3 | 21 | 0 | 360 | 2520 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12QM5 |  | 12'12'12'12' | 48' QM5 | 1 |  | MD Fresh Meat | 66.96 | 23 | Off Cycle | 115 | 3 | 21 | 0 | 360 | 2520 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12QM5 |  | 8'8'12'12'12' | 52' QM5 | 1 |  | MD Fresh Meat | 72.54 | 23 | Off Cycle | 115 | 3.25 | 22.75 | 0 | 390 | 2730 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12QM5 |  | 8'12'12'12'12 | 56' QM5 | 1 |  | MD Fresh Meat | 78.12 | 23 | Off Cycle | 115 | 3.5 | 24.5 | 0 | 420 | 2940 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | QD6 Deli Meat | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QD6 |  | 4' | 4'QD6 | 1 |  | MD Deli Meat | 5.2 | 23 | Off Cycle | 115 | 0.25 | 0.46 | 0 | 30 | 55.2 | 0 |  |  | SORIT 12
6QD6 |  | 6' | 6'QD6 | 1 |  | MD Deli Meat | 7.8 | 23 | Off Cycle | 115 | 0.4 | 0.92 | 0 | 48 | 110.4 | 0 |  |  | SORIT 12
8QD6 |  | 8' | 8'QD6 | 1 |  | MD Deli Meat | 10.4 | 23 | Off Cycle | 115 | 0.5 | 0.92 | 0 | 60 | 110.4 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12QD6 |  | 12' | 12'QD6 | 1 |  | MD Deli Meat | 15.6 | 23 | Off Cycle | 115 | 0.75 | 1.48 | 0 | 90 | 177.6 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8QD6 |  | 8'8' | 16' QD6 | 1 |  | MD Deli Meat | 20.8 | 23 | Off Cycle | 115 | 1 | 1.84 | 0 | 120 | 220.8 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12QD6 |  | 8'12' | 20' QD6 | 1 |  | MD Deli Meat | 26 | 23 | Off Cycle | 115 | 1.25 | 2.4 | 0 | 150 | 288 | 0 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8QD6 |  | 8'8'8' | 24' QD6 | 1 |  | MD Deli Meat | 31.2 | 23 | Off Cycle | 115 | 1.5 | 2.76 | 0 | 180 | 331.2 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12QD6 |  | 12'12' | 24' QD6 | 1 |  | MD Deli Meat | 31.2 | 23 | Off Cycle | 115 | 1.5 | 2.96 | 0 | 180 | 355.2 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'12QD6 |  | 8'8'12' | 28' QD6 | 1 |  | MD Deli Meat | 36.4 | 23 | Off Cycle | 115 | 1.75 | 3.32 | 0 | 210 | 398.4 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8QD6 |  | 8'8'8'8' | 32' QD6 | 1 |  | MD Deli Meat | 41.6 | 23 | Off Cycle | 115 | 2 | 3.68 | 0 | 240 | 441.6 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'12'12QD6 |  | 8'12'12' | 32' QD6 | 1 |  | MD Deli Meat | 41.6 | 23 | Off Cycle | 115 | 2 | 3.88 | 0 | 240 | 465.6 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'12QD6 |  | 8'8'8'12' | 36' QD6 | 1 |  | MD Deli Meat | 46.8 | 23 | Off Cycle | 115 | 2.25 | 4.24 | 0 | 270 | 508.8 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
12'12'12QD6 |  | 12'12'12' | 36' QD6 | 1 |  | MD Deli Meat | 46.8 | 23 | Off Cycle | 115 | 2.25 | 4.44 | 0 | 270 | 532.8 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'8'8QD6 |  | 8'8'8'8'8' | 40' QD6 | 1 |  | MD Deli Meat | 52 | 23 | Off Cycle | 115 | 2.5 | 4.6 | 0 | 300 | 552 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12QD6 |  | 8'8'12'12' | 40' QD6 | 1 |  | MD Deli Meat | 52 | 23 | Off Cycle | 115 | 2.5 | 4.8 | 0 | 300 | 576 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12QD6 |  | 8'8'8'8'12' | 44' QD6 | 1 |  | MD Deli Meat | 57.2 | 23 | Off Cycle | 115 | 2.75 | 5.16 | 0 | 330 | 619.2 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12QD6 |  | 8'12'12'12' | 44' QD6 | 1 |  | MD Deli Meat | 57.2 | 23 | Off Cycle | 115 | 2.75 | 5.36 | 0 | 330 | 643.2 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12QD6 |  | 8'8'8'12'12' | 48' QD6 | 1 |  | MD Deli Meat | 62.4 | 23 | Off Cycle | 115 | 3 | 5.72 | 0 | 360 | 686.4 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12QD6 |  | 12'12'12'12' | 48' QD6 | 1 |  | MD Deli Meat | 62.4 | 23 | Off Cycle | 115 | 3 | 5.92 | 0 | 360 | 710.4 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12QD6 |  | 8'8'12'12'12' | 52' QD6 | 1 |  | MD Deli Meat | 67.6 | 23 | Off Cycle | 115 | 3.25 | 6.28 | 0 | 390 | 753.6 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12QD6 |  | 8'12'12'12'12 | 56' QD6 | 1 |  | MD Deli Meat | 72.8 | 23 | Off Cycle | 115 | 3.5 | 6.84 | 0 | 420 | 820.8 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | QD6L Produce, Dairy and Beverage | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QD6L |  | 4' | 4'QD6L | 1 |  | MD Dairy | 5.54 | 23 | Off Cycle | 115 | 0.25 | 0.46 | 0 | 30 | 55.2 | 0 |  |  | SORIT 12
6QD6L |  | 6' | 6'QD6L | 1 |  | MD Dairy | 8.31 | 23 | Off Cycle | 115 | 0.4 | 0.92 | 0 | 48 | 110.4 | 0 |  |  | SORIT 12
8QD6L |  | 8' | 8'QD6L | 1 |  | MD Dairy | 11.08 | 23 | Off Cycle | 115 | 0.5 | 0.92 | 0 | 60 | 110.4 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12QD6L |  | 12' | 12'QD6L | 1 |  | MD Dairy | 16.62 | 23 | Off Cycle | 115 | 0.75 | 1.48 | 0 | 90 | 177.6 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8QD6L |  | 8'8' | 16' QD6L | 1 |  | MD Dairy | 22.16 | 23 | Off Cycle | 115 | 1 | 1.84 | 0 | 120 | 220.8 | 0 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12QD6L |  | 8'12' | 20' QD6L | 1 |  | MD Dairy | 27.7 | 23 | Off Cycle | 115 | 1.25 | 2.4 | 0 | 150 | 288 | 0 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8QD6L |  | 8'8'8' | 24' QD6L | 1 |  | MD Dairy | 33.24 | 23 | Off Cycle | 115 | 1.5 | 2.76 | 0 | 180 | 331.2 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12QD6L |  | 12'12' | 24' QD6L | 1 |  | MD Dairy | 33.24 | 23 | Off Cycle | 115 | 1.5 | 2.96 | 0 | 180 | 355.2 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'12QD6L |  | 8'8'12' | 28' QD6L | 1 |  | MD Dairy | 38.78 | 23 | Off Cycle | 115 | 1.75 | 3.32 | 0 | 210 | 398.4 | 0 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8QD6L |  | 8'8'8'8' | 32' QD6L | 1 |  | MD Dairy | 44.32 | 23 | Off Cycle | 115 | 2 | 3.68 | 0 | 240 | 441.6 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'12'12QD6L |  | 8'12'12' | 32' QD6L | 1 |  | MD Dairy | 44.32 | 23 | Off Cycle | 115 | 2 | 3.88 | 0 | 240 | 465.6 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'12QD6L |  | 8'8'8'12' | 36' QD6L | 1 |  | MD Dairy | 49.86 | 23 | Off Cycle | 115 | 2.25 | 4.24 | 0 | 270 | 508.8 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
12'12'12QD6L |  | 12'12'12' | 36' QD6L | 1 |  | MD Dairy | 49.86 | 23 | Off Cycle | 115 | 2.25 | 4.44 | 0 | 270 | 532.8 | 0 |  |  | SORIT 20 |  |  | 7/8 | 5/8
8'8'8'8'8QD6L |  | 8'8'8'8'8' | 40' QD6L | 1 |  | MD Dairy | 55.4 | 23 | Off Cycle | 115 | 2.5 | 4.6 | 0 | 300 | 552 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12QD6L |  | 8'8'12'12' | 40' QD6L | 1 |  | MD Dairy | 55.4 | 23 | Off Cycle | 115 | 2.5 | 4.8 | 0 | 300 | 576 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12QD6L |  | 8'8'8'8'12' | 44' QD6L | 1 |  | MD Dairy | 60.94 | 23 | Off Cycle | 115 | 2.75 | 5.16 | 0 | 330 | 619.2 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12QD6L |  | 8'12'12'12' | 44' QD6L | 1 |  | MD Dairy | 60.94 | 23 | Off Cycle | 115 | 2.75 | 5.36 | 0 | 330 | 643.2 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12QD6L |  | 8'8'8'12'12' | 48' QD6L | 1 |  | MD Dairy | 66.48 | 23 | Off Cycle | 115 | 3 | 5.72 | 0 | 360 | 686.4 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12QD6L |  | 12'12'12'12' | 48' QD6L | 1 |  | MD Dairy | 66.48 | 23 | Off Cycle | 115 | 3 | 5.92 | 0 | 360 | 710.4 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12QD6L |  | 8'8'12'12'12' | 52' QD6L | 1 |  | MD Dairy | 72.02 | 23 | Off Cycle | 115 | 3.25 | 6.28 | 0 | 390 | 753.6 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12QD6L |  | 8'12'12'12'12 | 56' QD6L | 1 |  | MD Dairy | 77.56 | 23 | Off Cycle | 115 | 3.5 | 6.84 | 0 | 420 | 820.8 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | HQDD6 Deli, Dairy and Beverage | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4HQDD6 |  | 4' | 4'HQDD6 | 1 |  | MD Door | 1.272 | 30 | Off Cycle | 115 | 0.25 | 0.56 | 0.61 | 30 | 67.2 | 73.2 |  |  | SORIT 12
30
8HQDD6 |  | 8' | 8'HQDD6 | 1 |  | MD Door | 2.544 | 30 | Off Cycle | 115 | 0.5 | 1.44 | 1.22 | 60 | 172.8 | 146.4 |  |  | SORIT 12
12HQDD6 |  | 12' | 12'HQDD6 | 1 |  | MD Door | 3.816 | 30 | Off Cycle | 115 | 0.75 | 1.82 | 1.82 | 90 | 218.4 | 218.4 |  |  | SORIT 12
8'8HQDD6 |  | 8'8' | 16' HQDD6 | 1 |  | MD Door | 5.088 | 30 | Off Cycle | 115 | 1 | 2.88 | 2.44 | 120 | 345.6 | 292.8 |  |  | SORIT 12
8'12HQDD6 |  | 8'12' | 20' HQDD6 | 1 |  | MD Door | 6.36 | 30 | Off Cycle | 115 | 1.25 | 3.26 | 3.04 | 150 | 391.2 | 364.8 |  |  | SORIT 12
8'8'8HQDD6 |  | 8'8'8' | 24' HQDD6 | 1 |  | MD Door | 7.632 | 30 | Off Cycle | 115 | 1.5 | 4.32 | 3.66 | 180 | 518.4 | 439.2 |  |  | SORIT 12
12'12HQDD6 |  | 12'12' | 24' HQDD6 | 1 |  | MD Door | 7.632 | 30 | Off Cycle | 115 | 1.5 | 3.64 | 3.64 | 180 | 436.8 | 436.8 |  |  | SORIT 12
8'8'12HQDD6 |  | 8'8'12' | 28' HQDD6 | 1 |  | MD Door | 8.904 | 30 | Off Cycle | 115 | 1.75 | 4.7 | 4.26 | 210 | 564 | 511.2 |  |  | SORIT 12
8'8'8'8HQDD6 |  | 8'8'8'8' | 32' HQDD6 | 1 |  | MD Door | 10.176 | 30 | Off Cycle | 115 | 2 | 5.76 | 4.88 | 240 | 691.2 | 585.6 |  |  | SORIT 12
8'12'12HQDD6 |  | 8'12'12' | 32' HQDD6 | 1 |  | MD Door | 10.176 | 30 | Off Cycle | 115 | 2 | 5.08 | 4.86 | 240 | 609.6 | 583.2 |  |  | SORIT 12
8'8'8'12HQDD6 |  | 8'8'8'12' | 36' HQDD6 | 1 |  | MD Door | 11.448 | 30 | Off Cycle | 115 | 2.25 | 6.14 | 5.48 | 270 | 736.8 | 657.6 |  |  | SORIT 12
12'12'12HQDD6 |  | 12'12'12' | 36' HQDD6 | 1 |  | MD Door | 11.448 | 30 | Off Cycle | 115 | 2.25 | 5.46 | 5.46 | 270 | 655.2 | 655.2 |  |  | SORIT 12
8'8'8'8'8HQDD6 |  | 8'8'8'8'8' | 40' HQDD6 | 1 |  | MD Door | 12.72 | 30 | Off Cycle | 115 | 2.5 | 7.2 | 6.1 | 300 | 864 | 732 |  |  | SORIT 12
8'8'12'12HQDD6 |  | 8'8'12'12' | 40' HQDD6 | 1 |  | MD Door | 12.72 | 30 | Off Cycle | 115 | 2.5 | 6.52 | 6.08 | 300 | 782.4 | 729.6 |  |  | SORIT 12
8'8'8'8'12HQDD6 |  | 8'8'8'8'12' | 44' HQDD6 | 1 |  | MD Door | 13.992 | 30 | Off Cycle | 115 | 2.75 | 7.58 | 6.7 | 330 | 909.6 | 804 |  |  | SORIT 12
8'12'12'12HQDD6 |  | 8'12'12'12' | 44' HQDD6 | 1 |  | MD Door | 13.992 | 30 | Off Cycle | 115 | 2.75 | 6.9 | 6.68 | 330 | 828 | 801.6 |  |  | SORIT 12
8'8'8'12'12HQDD6 |  | 8'8'8'12'12' | 48' HQDD6 | 1 |  | MD Door | 15.264 | 30 | Off Cycle | 115 | 3 | 7.96 | 7.3 | 360 | 955.2 | 876 |  |  | SORIT 12
12'12'12'12HQDD6 |  | 12'12'12'12' | 48' HQDD6 | 1 |  | MD Door | 15.264 | 30 | Off Cycle | 115 | 3 | 7.28 | 7.28 | 360 | 873.6 | 873.6 |  |  | SORIT 12
8'8'12'12'12HQDD6 |  | 8'8'12'12'12' | 52' HQDD6 | 1 |  | MD Door | 16.536 | 30 | Off Cycle | 115 | 3.25 | 8.34 | 7.9 | 390 | 1000.8 | 948 |  |  | SORIT 12
8'12'12'12'12HQDD6 |  | 8'12'12'12'12 | 56' HQDD6 | 1 |  | MD Door | 17.808 | 30 | Off Cycle | 115 | 3.5 | 8.72 | 8.5 | 420 | 1046.4 | 1020 |  |  | SORIT 12
|  | QS2AG | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4QS2AG |  | 4' | 4' QS2AG | 1 |  | 3D Meat | 3.916 | 24 | Off Cycle | 115 | 0.2 | 0.75 | 0.1 | 24 | 90 | 12 |  |  | SORIT 12
6QS2AG |  | 6' | 6' QS2AG | 1 |  | 3D Meat | 5.874 | 24 | Off Cycle | 115 | 0.4 | 1.3 | 0.16 | 48 | 156 | 19.2 |  |  | SORIT 12
8QS2AG |  | 8' | 8' QS2AG | 1 |  | 3D Meat | 7.832 | 24 | Off Cycle | 115 | 0.4 | 1.5 | 0.24 | 48 | 180 | 28.8 |  |  | SORIT 12 |  |  | 1/2 | 1/2
12QS2AG |  | 12' | 12' QS2AG | 1 |  | 3D Meat | 11.748 | 24 | Off Cycle | 115 | 0.6 | 2.25 | 0.32 | 72 | 270 | 38.4 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'8QS2AG |  | 8'8' | 16' QS2AG | 1 |  | 3D Meat | 15.664 | 24 | Off Cycle | 115 | 0.8 | 3 | 0.48 | 96 | 360 | 57.6 |  |  | SORIT 12 |  |  | 5/8 | 5/8
8'12QS2AG |  | 8'12' | 20' QS2AG | 1 |  | 3D Meat | 19.58 | 24 | Off Cycle | 115 | 1 | 3.75 | 0.56 | 120 | 450 | 67.2 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8QS2AG |  | 8'8'8' | 24' QS2AG | 1 |  | 3D Meat | 23.496 | 24 | Off Cycle | 115 | 1.2 | 4.5 | 0.72 | 144 | 540 | 86.4 |  |  | SORIT 12 |  |  | 7/8 | 5/8
12'12QS2AG |  | 12'12' | 24' QS2AG | 1 |  | 3D Meat | 23.496 | 24 | Off Cycle | 115 | 1.2 | 4.5 | 0.64 | 144 | 540 | 76.8 |  |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'12QS2AG |  | 8'8'12' | 28' QS2AG | 1 |  | 3D Meat | 27.412 | 24 | Off Cycle | 115 | 1.4 | 5.25 | 0.8 | 168 | 630 | 96 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8QS2AG |  | 8'8'8'8' | 32' QS2AG | 1 |  | 3D Meat | 31.328 | 24 | Off Cycle | 115 | 1.6 | 6 | 0.96 | 192 | 720 | 115.2 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'12'12QS2AG |  | 8'12'12' | 32' QS2AG | 1 |  | 3D Meat | 31.328 | 24 | Off Cycle | 115 | 1.6 | 6 | 0.88 | 192 | 720 | 105.6 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'12QS2AG |  | 8'8'8'12' | 36' QS2AG | 1 |  | 3D Meat | 35.244 | 24 | Off Cycle | 115 | 1.8 | 6.75 | 1.04 | 216 | 810 | 124.8 |  |  | SORIT 15 |  |  | 7/8 | 5/8
12'12'12QS2AG |  | 12'12'12' | 36' QS2AG | 1 |  | 3D Meat | 35.244 | 24 | Off Cycle | 115 | 1.8 | 6.75 | 0.96 | 216 | 810 | 115.2 |  |  | SORIT 15 |  |  | 7/8 | 5/8
8'8'8'8'8QS2AG |  | 8'8'8'8'8' | 40' QS2AG | 1 |  | 3D Meat | 39.16 | 24 | Off Cycle | 115 | 2 | 7.5 | 1.2 | 240 | 900 | 144 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12QS2AG |  | 8'8'12'12' | 40' QS2AG | 1 |  | 3D Meat | 39.16 | 24 | Off Cycle | 115 | 2 | 7.5 | 1.12 | 240 | 900 | 134.4 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'12QS2AG |  | 8'8'8'8'12' | 44' QS2AG | 1 |  | 3D Meat | 43.076 | 24 | Off Cycle | 115 | 2.2 | 8.25 | 1.28 | 264 | 990 | 153.6 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12QS2AG |  | 8'12'12'12' | 44' QS2AG | 1 |  | 3D Meat | 43.076 | 24 | Off Cycle | 115 | 2.2 | 8.25 | 1.2 | 264 | 990 | 144 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12QS2AG |  | 8'8'8'12'12' | 48' QS2AG | 1 |  | 3D Meat | 46.992 | 24 | Off Cycle | 115 | 2.4 | 9 | 1.36 | 288 | 1080 | 163.2 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12QS2AG |  | 12'12'12'12' | 48' QS2AG | 1 |  | 3D Meat | 46.992 | 24 | Off Cycle | 115 | 2.4 | 9 | 1.28 | 288 | 1080 | 153.6 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12'12QS2AG |  | 8'8'12'12'12' | 52' QS2AG | 1 |  | 3D Meat | 50.908 | 24 | Off Cycle | 115 | 2.6 | 9.75 | 1.44 | 312 | 1170 | 172.8 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12'12QS2AG |  | 8'12'12'12'12 | 56' QS2AG | 1 |  | 3D Meat | 54.824 | 24 | Off Cycle | 115 | 2.8 | 10.5 | 1.52 | 336 | 1260 | 182.4 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'62QS2AG |  | 8'8'8'8'6' | 38' QS2AG | 1 |  | 3D Meat Island | 37.202 | 24 | Off Cycle | 115 | 2 | 7.3 | 1.12 | 240 | 876 | 134.4 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | BARKER | Including Cases for BLOOMS | [14 empty] | 90
[8 empty] | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
|  | Frozen Cake and Frozen Natures |  | PER GREG WILSONS |  | EMAIL DATED 08/12/05
CAKE/FROZEN NATURE
6BDPTD-6R |  | 6' | BDPTD-6R |  |  | Cake Case | 6.87 | -15 | Hot Gas | 115 | 1.1 | 1.47 |  | 126.5 | 169.05 | 0 | E14S250 |  | SORIT 12
6BDPT-6R |  | 6' | BDPT-6R |  |  | Lowboy Cake | 6 | -15 | Hot Gas | 115 | 1.1 | 1.47 |  | 126.5 | 169.05 | 0 | E14S250 |  | SORIT 12
8BDPF-8RLT54 |  | 8' | BDPF-8RLT54 |  |  | Cake & Cheese | 9.2 | -15 | Hot Gas | 115 | 1.65 | 1.41 |  | 189.75 | 162.15 | 0 | E14S250 |  | SORIT 12
6BDPT |  | 6' | BDPT-6R |  |  | Workstation | 6.98 | -15 | Hot Gas | 115 | 1.1 | 0.98 |  | 126.5 | 112.7 | 0 | E14S250 |  | SORIT 12
5S-132-24L-LT |  | 5' | S-132-24L-LT |  |  | Frozen Natures Place - Slim | 8.53 | -20 | Hot Gas | 115 | 3.3 | 3.76 |  | 379.5 | 432.4 | 0 | E14S250 |  | SORIT 12
3 Dr SS-77-24R-LT |  | 3' | S-77-24R-LT |  |  | Frozen Natures Place - Slim | 4.8 | -20 | Hot Gas | 115 | 1.1 | 2.1 |  | 126.5 | 241.5 | 0 | E14S250 |  | SORIT 12
5 Dr S-132-24L-LT |  | 5' | S-132-24L-LT |  |  | Frozen Natues Place - Slim | 8.5 | -20 | Hot Gas | 115 | 3.3 | 3.76 |  | 379.5 | 432.4 | 0 | E14S250 |  | SORIT 12
CAKE/CHEESE/SALAD
8BDPF |  | 8' | BDPF-8R |  |  | Cake & Cheese | 9.2 | 26 | Off Cycle | 115 | 1.65 | 1.88 |  | 189.75 | 216.2 | 0 |  |  | SORIT 12
10BDPF-10R |  | 10' | BDPF-10R |  |  | Cake & Cheese | 11.5 | 26 | Off Cycle | 115 | 2.2 | 2.58 |  | 253 | 296.7 | 0 |  |  | SORIT 12
12BDPTD-12R |  | 12 | BDPTD-12R |  |  | Cake & Cheese | 13.8 | 26 | Off Cycle | 115 | 2.2 | 2.78 |  | 253 | 319.7 | 0 |  |  | SORIT 12
8BDPTD-8 |  | 8 | BDPTD-8R |  |  | Bulk Salad | 9.16 | 26 | Off Cycle | 115 | 1.65 | 1.47 |  | 189.75 | 169.05 | 0 |  |  | SORIT 12
4BDPT-4RRS |  | 4 | BDPT-4RRS |  |  | Sushi | 3.98 | 26 | Off Cycle | 115 | 0.55 | 0.98 |  | 63.25 | 112.7 | 0 |  |  | SORIT 12
4BDPF |  | 4 | BDPF-4R54 |  |  | Salad/Sandwich | 3.78 | 26 | Off Cycle | 115 | 0.55 | 0.98 |  | 63.25 | 112.7 | 0 |  |  | SORIT 12
WINE/NATURES PLACE
4BDPF-4R54 |  | 4 | BDPF-4R54 |  |  | Wine | 4.6 | 45 | Off Cycle | 115 | 0.3 | 0.91 |  | 34.5 | 104.65 | 0 |  |  | SORIT 12
4BDPF-4R62 |  | 4 | BDPF-4R62 |  |  | Wine | 5.2 | 45 | Off Cycle | 115 | 0.3 | 0.91 |  | 34.5 | 104.65 | 0 |  |  | SORIT 12
4BDPF-4R72 |  | 4 | BDPF-4R72 |  |  | Wine | 6 | 45 | Off Cycle | 115 | 0.3 | 0.91 |  | 34.5 | 104.65 | 0 |  |  | SORIT 12
SEAFOOD
8BDPTD-8R |  | 8 | BDPTD-8R |  |  | Seafood Service Combo | 8 | 26 | Off Cycle | 115 | 1.8 | 1.24 |  | 207 | 142.6 | 0 |  |  | SORIT 12
5BSDT-5R |  | 5 | BSDT-5R |  |  | Seafood Service | 2.25 | 22 | Off Cycle | 115 | 1.1 |  |  | 126.5 | 0 | 0 |  |  | SORIT 12
FLORAL/PRODUCE
NFTHSO |  | 6'/8' | NFT/HSO |  |  | Floral / Prod. Table | 13.3 | 22 | Off Cycle | 115 | 2.5 | 2.7 |  | 287.5 | 310.5 | 0 |  |  | SORIT 12
8HSO |  | 8' | HSO |  |  | Produce Table | 6.4 | 22 | Off Cycle | 115 | 1.1 | 0.49 |  | 126.5 | 56.35 | 0 |  |  | SORIT 12 |  |  |  | 1/2
6NFD |  | 6' | NFD-3 |  |  | Floral with 3 doors | 4.8 | 22 | Off Cycle | 115 | 2.2 | 1.9 |  | 253 | 218.5 | 0 |  |  | SORIT 12
6NFO |  | 6' | NFO-6 |  |  | Floral w/o Doors | 9 | 22 | Off Cycle | 115 | 1.65 | 0.76 |  | 189.75 | 87.4 | 0 |  |  | SORIT 12
NFT-2 |  | 4' | NFT-2 |  |  | Floral Combo | 4.6 | 22 | Off Cycle | 115 | 0.81 | 1.17 |  | 93.15 | 134.55
NFT-3 |  | 6' | NFT-3 |  |  | Floral Combo | 6.9 | 22 | Off Cycle | 115 | 1.88 | 2.35 |  | 216.2 | 270.25 | 0 |  |  | SORIT 12
NFT-4 |  | 8' | NFT-4 |  |  | Floral Combo | 9.2 | 22 | Off Cycle | 115 | 1.88 | 2.35 |  | 216.2 | 270.25
FT-4R |  | 4' | FT-4R NRG |  |  | Floral | 3.78 | 26 | Off Cycle | 115 | 0.3 | 0.3 |  | 34.5 | 34.5 | 0 |  |  | SORIT 12
FT-6R |  | 6' | FT-6R NRG |  |  | Floral | 5.67 | 26 | Off Cycle | 115 | 1.59 | 0.5 |  | 182.85 | 57.5 | 0 |  |  | SORIT 12
CHEESE
6PFI-506-48R |  | 6 | PFI-508-48R |  |  | Cheese Island | 9.45 | 26 | Off Cycle | 115 | 1.89 | 3.1 |  | 217.35 | 356.5 | 0 |  |  | SORIT 12
8PFI-508 |  | 8 | PFI-508 |  |  | Cheese Island | 15.12 | 26 | Off Cycle | 115 | 3.3 | 3.08 |  | 379.5 | 354.2 | 0 |  |  | SORIT 12
6CF |  | 6' | CF |  |  | Self Serve Deli | 5.7 | 20 | Off Cycle | 115 | 1.1 | 0.49 |  | 126.5 | 56.35 | 0 |  |  | SORIT 12
6BDPF-6R3S72 |  | 6 | BDPF-6R3S72 |  |  | Three Sided Cheese Mdse | 9.54 | 26 | Off Cycle | 115 | 3.3 | 3.57 |  | 379.5 | 410.55 | 0 |  |  | SORIT 12
NRG COILS
[11 empty] | FAN | LIGHT | A/S
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
6PT72Cake |  | 6' | PT72 |  |  | Cake | 6.324 | 24 | Off Cycle | 115 | 0.91 | 2.04 |  | 109.2 | 244.8 | 0 |  |  | SORIT 12
8PT72Cake |  | 8' | PT72 |  |  | Cake | 8.432 | 24 | Off Cycle | 115 | 1.2 | 2.82 |  | 144 | 338.4 | 0 |  |  | SORIT 12
[9 empty] | Off Cycle | 115 |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
8PTD54RRS |  | 8' | PTD54RRS |  |  | Deli | 6.64 | 24 | Off Cycle | 115 | 1.3 | 1.41 | 0.42 | 156 | 169.2 | 50.4 |  |  | SORIT 12
12PTD54RRS |  | 12' | PTD54RRS |  |  | Deli | 9.96 | 24 | Off Cycle | 115 | 1.72 | 2.1 | 0.62 | 206.4 | 252 | 74.4 |  |  | SORIT 12
6PT51 |  | 6' | PT51 |  |  | Deli | 5 | 24 | Off Cycle | 115 | 0.9 | 1.36 |  | 108 | 163.2 | 0 |  |  | SORIT 12
8PT51 |  | 8' | PT51 |  |  | Deli | 6.68 | 24 | Off Cycle | 115 | 0.9 | 1.9 |  | 108 | 228 | 0 |  |  | SORIT 12
6PT54 |  | 6' | PT54 |  |  | Deli | 5.544 | 24 | Off Cycle | 115 | 0.9 | 1.36 |  | 108 | 163.2 | 0 |  |  | SORIT 12
8PT54 |  | 8' | PT54 |  |  | Deli | 7.392 | 24 | Off Cycle | 115 | 0.9 | 1.88 |  | 108 | 225.6 | 0 |  |  | SORIT 12
10PT54 |  | 10' | PT54 |  |  | Deli | 9.24 | 24 | Off Cycle | 115 | 1.2 | 2.44 |  | 144 | 292.8 | 0 |  |  | SORIT 12
12PT54 |  | 12' | PT54 |  |  | Deli | 11.088 | 24 | Off Cycle | 115 | 1.2 | 2.76 |  | 144 | 331.2 | 0 |  |  | SORIT 12
[9 empty] | Off Cycle | 115 |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
6PT67 |  | 6' | PT67 |  |  | Deli | 6.324 | 24 | Off Cycle | 115 | 0.91 | 2.04 |  | 109.2 | 244.8 | 0 |  |  | SORIT 12
8PT67 |  | 8' | PT67 |  |  | Deli | 8.432 | 24 | Off Cycle | 115 | 1.2 | 2.82 |  | 144 | 338.4 | 0 |  |  | SORIT 12
10PT67 |  | 10' | PT67 |  |  | Deli | 10.54 | 24 | Off Cycle | 115 | 1.5 | 3.66 |  | 180 | 439.2 | 0 |  |  | SORIT 12
12PT67 |  | 12' | PT67 |  |  | Deli | 12.648 | 24 | Off Cycle | 115 | 1.8 | 4.14 |  | 216 | 496.8 | 0 |  |  | SORIT 12
[9 empty] | Off Cycle | 115 |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
6HTPT67 |  | 6' | HTPT67 |  |  | Deli Cold/Hot | 4.8 | 24 | Off Cycle | 115 | 0.9 | 0.9 |  | 108 | 108 | 0 |  |  | SORIT 12
8HTPT67 |  | 8' | HTPT67 |  |  | Deli Cold/Hot | 6.4 | 24 | Off Cycle | 115 | 0.9 | 0.94 |  | 108 | 112.8 | 0 |  |  | SORIT 12
10HTPT67 |  | 10' | HTPT67 |  |  | Deli Cold/Hot | 8 | 24 | Off Cycle | 115 | 1.2 | 1.22 |  | 144 | 146.4 | 0 |  |  | SORIT 12
9TY3 |  | 9' | TY3-5 |  |  | Deli Island | 13.79 | 24 | Off Cycle | 115 | 1.8 | 3 | 0.74 | 216 | 360 | 88.8 |  |  | SORIT 12
8TY4 |  | 8' | TY4-4 |  |  | Deli Island | 15.3 | 24 | Off Cycle | 115 | 1.8 | 3 | 0.42 | 216 | 360 | 50.4 |  |  | SORIT 12
8'8TY4 |  | 8'8' | 16' TY4-4 |  |  | Deli Island | 30.6 | 24 | Off Cycle | 115 | 3.6 | 6 | 0.84 | 432 | 720 | 100.8 |  |  | SORIT 12
|  | QLV5V | FROZEN FOOD | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QLV5V |  | 2 | QLV5V | 1 |  | Frozen Food | 2.75 | -11 | HG 2 Wire | 115 | 0.5 | 1.39 | 3.67 | 60 | 166.8 | 440.4 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QLV5V |  | 3 | QLV5V | 1 |  | Frozen Food | 4.125 | -11 | HG 2 Wire | 115 | 0.75 | 1.8 | 4.73 | 90 | 216 | 567.6 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QLV5V |  | 4 | QLV5V | 1 |  | Frozen Food | 5.5 | -11 | HG 2 Wire | 115 | 1 | 2.32 | 6.25 | 120 | 278.4 | 750 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QLV5V |  | 5 | QLV5V | 1 |  | Frozen Food | 6.875 | -11 | HG 2 Wire | 115 | 1.25 | 2.79 | 7.69 | 150 | 334.8 | 922.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QLV5V |  | 3,3 | 6Dr QLV5V | 1 |  | Frozen Food | 8.25 | -11 | HG 2 Wire | 115 | 1.5 | 3.6 | 9.46 | 180 | 432 | 1135.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QLV5V |  | 4,3 | 7Dr QLV5V | 1 |  | Frozen Food | 9.625 | -11 | HG 2 Wire | 115 | 1.75 | 4.12 | 10.98 | 210 | 494.4 | 1317.6 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QLV5V |  | 4,4 | 8Dr QLV5V | 1 |  | Frozen Food | 11 | -11 | HG 2 Wire | 115 | 2 | 4.64 | 12.5 | 240 | 556.8 | 1500 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QLV5V |  | 5,3 | 8Dr QLV5V | 1 |  | Frozen Food | 11 | -11 | HG 2 Wire | 115 | 2 | 4.59 | 12.42 | 240 | 550.8 | 1490.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QLV5V |  | 5,4 | 9Dr QLV5V | 1 |  | Frozen Food | 12.375 | -11 | HG 2 Wire | 115 | 2.25 | 5.11 | 13.94 | 270 | 613.2 | 1672.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QLV5V |  | 3,3,3 | 9Dr QLV5V | 1 |  | Frozen Food | 12.375 | -11 | HG 2 Wire | 115 | 2.25 | 5.4 | 14.19 | 270 | 648 | 1702.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QLV5V |  | 5,5 | 10Dr QLV5V | 1 |  | Frozen Food | 13.75 | -11 | HG 2 Wire | 115 | 2.5 | 5.58 | 15.38 | 300 | 669.6 | 1845.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QLV5V |  | 4,3,3 | 10Dr QLV5V | 1 |  | Frozen Food | 13.75 | -11 | HG 2 Wire | 115 | 2.5 | 5.92 | 15.71 | 300 | 710.4 | 1885.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QLV5V |  | 5,3,3 | 11Dr QLV5V | 1 |  | Frozen Food | 15.125 | -11 | HG 2 Wire | 115 | 2.75 | 6.39 | 17.15 | 330 | 766.8 | 2058 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3QLV5V |  | 4,4,3 | 11Dr QLV5V | 1 |  | Frozen Food | 15.125 | -11 | HG 2 Wire | 115 | 2.75 | 6.44 | 17.23 | 330 | 772.8 | 2067.6 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4QLV5V |  | 4,4,4 | 12Dr QLV5V | 1 |  | Frozen Food | 16.5 | -11 | HG 2 Wire | 115 | 3 | 6.96 | 18.75 | 360 | 835.2 | 2250 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3QLV5V |  | 5,4,3 | 12Dr QLV5V | 1 |  | Frozen Food | 16.5 | -11 | HG 2 Wire | 115 | 3 | 6.91 | 18.67 | 360 | 829.2 | 2240.4 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4QLV5V |  | 5,4,4 | 13Dr QLV5V | 1 |  | Frozen Food | 17.875 | -11 | HG 2 Wire | 115 | 3.25 | 7.43 | 20.19 | 390 | 891.6 | 2422.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QLV5V |  | 5,5,3 | 13Dr QLV5V | 1 |  | Frozen Food | 17.875 | -11 | HG 2 Wire | 115 | 3.25 | 7.38 | 20.11 | 390 | 885.6 | 2413.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QLV5V |  | 5,5,4 | 14Dr QLV5V | 1 |  | Frozen Food | 19.25 | -11 | HG 2 Wire | 115 | 3.5 | 7.9 | 21.63 | 420 | 948 | 2595.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QLV5V |  | 4,4,3,3 | 14Dr QLV5V | 1 |  | Frozen Food | 19.25 | -11 | HG 2 Wire | 115 | 3.5 | 8.24 | 21.96 | 420 | 988.8 | 2635.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QLV5V |  | 5,5,5 | 15Dr QLV5V | 1 |  | Frozen Food | 20.625 | -11 | HG 2 Wire | 115 | 3.75 | 8.37 | 23.07 | 450 | 1004.4 | 2768.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QLV5V |  | 4,4,4,3 | 15Dr QLV5V | 1 |  | Frozen Food | 20.625 | -11 | HG 2 Wire | 115 | 3.75 | 8.76 | 23.48 | 450 | 1051.2 | 2817.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QLV5V |  | 5,5,3,3 | 16Dr QLV5V | 1 |  | Frozen Food | 22 | -11 | HG 2 Wire | 115 | 4 | 9.18 | 24.84 | 480 | 1101.6 | 2980.8 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4QLV5V |  | 4,4,4,4 | 16Dr QLV5V | 1 |  | Frozen Food | 22 | -11 | HG 2 Wire | 115 | 4 | 9.28 | 25 | 480 | 1113.6 | 3000 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,3,2QLV5V | * | 4,3,2 | 9Dr QLV5V | 1 |  | Frozen Food | 12.375 | -11 | HG 2 Wire | 115 | 2.25 | 5.51 | 14.65 | 270 | 661.2 | 1758 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QLV5V | * | 5,3,2 | 10Dr QLV5V | 1 |  | Frozen Food | 13.75 | -11 | HG 2 Wire | 115 | 2.5 | 5.98 | 16.09 | 300 | 717.6 | 1930.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 39637
5,3,3,3QLV5V |  | 5,3,3,3 | 14Dr QLV5V | 1 |  | Frozen Food | 19.25 | -11 | HG 2 Wire | 115 | 3.5 | 8.19 | 21.88 | 420 | 982.8 | 2625.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QLV5V |  | 4,4,3,2 | 13Dr QLV5V | 1 |  | Frozen Food | 17.875 | -11 | HG 2 Wire | 115 | 3.25 | 7.83 | 20.9 | 390 | 939.6 | 2508 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QIV5V | ICE CREAM | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QIV5V |  | 2 | QIV5V | 1 |  | Ice Cream | 2.92 | -18 | HG 2 Wire | 115 | 0.5 | 1.39 | 3.67 | 60 | 166.8 | 440.4 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3QIV5V |  | 3 | QIV5V | 1 |  | Ice Cream | 4.38 | -18 | HG 2 Wire | 115 | 0.75 | 1.8 | 4.73 | 90 | 216 | 567.6 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4QIV5V |  | 4 | QIV5V | 1 |  | Ice Cream | 5.84 | -18 | HG 2 Wire | 115 | 1 | 2.32 | 6.25 | 120 | 278.4 | 750 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QIV5V |  | 5 | QIV5V | 1 |  | Ice Cream | 7.3 | -18 | HG 2 Wire | 115 | 1.25 | 2.79 | 7.69 | 150 | 334.8 | 922.8 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QIV5V |  | 3,3 | 6Dr QIV5V | 1 |  | Ice Cream | 8.76 | -18 | HG 2 Wire | 115 | 1.5 | 3.6 | 9.46 | 180 | 432 | 1135.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3QIV5V |  | 4,3 | 7Dr QIV5V | 1 |  | Ice Cream | 10.22 | -18 | HG 2 Wire | 115 | 1.75 | 4.12 | 10.98 | 210 | 494.4 | 1317.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4QIV5V |  | 4,4 | 8Dr QIV5V | 1 |  | Ice Cream | 11.68 | -18 | HG 2 Wire | 115 | 2 | 4.64 | 12.5 | 240 | 556.8 | 1500 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QIV5V |  | 5,3 | 8Dr QIV5V | 1 |  | Ice Cream | 11.68 | -18 | HG 2 Wire | 115 | 2 | 4.59 | 12.42 | 240 | 550.8 | 1490.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QIV5V |  | 5,4 | 9Dr QIV5V | 1 |  | Ice Cream | 13.14 | -18 | HG 2 Wire | 115 | 2.25 | 5.11 | 13.94 | 270 | 613.2 | 1672.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
3,3,3QIV5V |  | 3,3,3 | 9Dr QIV5V | 1 |  | Ice Cream | 13.14 | -18 | HG 2 Wire | 115 | 2.25 | 5.4 | 14.19 | 270 | 648 | 1702.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5QIV5V |  | 5,5 | 10Dr QIV5V | 1 |  | Ice Cream | 14.6 | -18 | HG 2 Wire | 115 | 2.5 | 5.58 | 15.38 | 300 | 669.6 | 1845.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3QIV5V |  | 4,3,3 | 10Dr QIV5V | 1 |  | Ice Cream | 14.6 | -18 | HG 2 Wire | 115 | 2.5 | 5.92 | 15.71 | 300 | 710.4 | 1885.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3QIV5V |  | 5,3,3 | 11Dr QIV5V | 1 |  | Ice Cream | 16.06 | -18 | HG 2 Wire | 115 | 2.75 | 6.39 | 17.15 | 330 | 766.8 | 2058 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3QIV5V |  | 4,4,3 | 11Dr QIV5V | 1 |  | Ice Cream | 16.06 | -18 | HG 2 Wire | 115 | 2.75 | 6.44 | 17.23 | 330 | 772.8 | 2067.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4QIV5V |  | 4,4,4 | 12Dr QIV5V | 1 |  | Ice Cream | 17.52 | -18 | HG 2 Wire | 115 | 3 | 6.96 | 18.75 | 360 | 835.2 | 2250 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3QIV5V |  | 5,4,3 | 12Dr QIV5V | 1 |  | Ice Cream | 17.52 | -18 | HG 2 Wire | 115 | 3 | 6.91 | 18.67 | 360 | 829.2 | 2240.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4QIV5V |  | 5,4,4 | 13Dr QIV5V | 1 |  | Ice Cream | 18.98 | -18 | HG 2 Wire | 115 | 3.25 | 7.43 | 20.19 | 390 | 891.6 | 2422.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QIV5V |  | 5,5,3 | 13Dr QIV5V | 1 |  | Ice Cream | 18.98 | -18 | HG 2 Wire | 115 | 3.25 | 7.38 | 20.11 | 390 | 885.6 | 2413.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QIV5V |  | 5,5,4 | 14Dr QIV5V | 1 |  | Ice Cream | 20.44 | -18 | HG 2 Wire | 115 | 3.5 | 7.9 | 21.63 | 420 | 948 | 2595.6 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,3QIV5V |  | 4,4,3,3 | 14Dr QIV5V | 1 |  | Ice Cream | 20.44 | -18 | HG 2 Wire | 115 | 3.5 | 8.24 | 21.96 | 420 | 988.8 | 2635.2 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,5QIV5V |  | 5,5,5 | 15Dr QIV5V | 1 |  | Ice Cream | 21.9 | -18 | HG 2 Wire | 115 | 3.75 | 8.37 | 23.07 | 450 | 1004.4 | 2768.4 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3QIV5V |  | 4,4,4,3 | 15Dr QIV5V | 1 |  | Ice Cream | 21.9 | -18 | HG 2 Wire | 115 | 3.75 | 8.76 | 23.48 | 450 | 1051.2 | 2817.6 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3QIV5V |  | 5,5,3,3 | 16Dr QIV5V | 1 |  | Ice Cream | 23.36 | -18 | HG 2 Wire | 115 | 4 | 9.18 | 24.84 | 480 | 1101.6 | 2980.8 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4QIV5V |  | 4,4,4,4 | 16Dr QIV5V | 1 |  | Ice Cream | 23.36 | -18 | HG 2 Wire | 115 | 4 | 9.28 | 25 | 480 | 1113.6 | 3000 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,2QIV5V |  | 4,4,3,2 | 13Dr QIV5V | 1 |  | Ice Cream | 18.98 | -18 | HG 2 Wire | 115 | 3.25 | 7.83 | 20.9 | 390 | 939.6 | 2508 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QFGCEI | FROZEN FOOD | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEIFF |  | 2 | QFGCEI | 1 |  | Frozen Food | 2.75 | -10 | HG 2 Wire | 115 | 0.5 | 1.39 | 3.63 | 60 | 166.8 | 435.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEIFF |  | 3 | QFGCEI | 1 |  | Frozen Food | 4.125 | -10 | HG 2 Wire | 115 | 0.75 | 1.8 | 5.25 | 90 | 216 | 630 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEIFF |  | 4 | QFGCEI | 1 |  | Frozen Food | 5.5 | -10 | HG 2 Wire | 115 | 1 | 2.32 | 7.02 | 120 | 278.4 | 842.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEIFF |  | 5 | QFGCEI | 1 |  | Frozen Food | 6.875 | -10 | HG 2 Wire | 115 | 1.25 | 2.79 | 8.61 | 150 | 334.8 | 1033.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEIFF |  | 3,3 | 6Dr QFGCEI | 1 |  | Frozen Food | 8.25 | -10 | HG 2 Wire | 115 | 1.5 | 3.6 | 10.5 | 180 | 432 | 1260 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEIFF |  | 4,3 | 7Dr QFGCEI | 1 |  | Frozen Food | 9.625 | -10 | HG 2 Wire | 115 | 1.75 | 4.12 | 12.27 | 210 | 494.4 | 1472.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEIFF |  | 4,4 | 8Dr QFGCEI | 1 |  | Frozen Food | 11 | -10 | HG 2 Wire | 115 | 2 | 4.64 | 14.04 | 240 | 556.8 | 1684.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEIFF |  | 5,3 | 8Dr QFGCEI | 1 |  | Frozen Food | 11 | -10 | HG 2 Wire | 115 | 2 | 4.59 | 13.86 | 240 | 550.8 | 1663.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEIFF |  | 5,4 | 9Dr QFGCEI | 1 |  | Frozen Food | 12.375 | -10 | HG 2 Wire | 115 | 2.25 | 5.11 | 15.63 | 270 | 613.2 | 1875.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEIFF |  | 3,3,3 | 9Dr QFGCEI | 1 |  | Frozen Food | 12.375 | -10 | HG 2 Wire | 115 | 2.25 | 5.4 | 15.75 | 270 | 648 | 1890 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEIFF |  | 5,5 | 10Dr QFGCEI | 1 |  | Frozen Food | 13.75 | -10 | HG 2 Wire | 115 | 2.5 | 5.58 | 17.22 | 300 | 669.6 | 2066.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QFGCEIFF |  | 4,3,3 | 10Dr QFGCEI | 1 |  | Frozen Food | 13.75 | -10 | HG 2 Wire | 115 | 2.5 | 5.92 | 17.52 | 300 | 710.4 | 2102.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QFGCEIFF |  | 5,3,3 | 11Dr QFGCEI | 1 |  | Frozen Food | 15.125 | -10 | HG 2 Wire | 115 | 2.75 | 6.39 | 19.11 | 330 | 766.8 | 2293.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3QFGCEIFF |  | 4,4,3 | 11Dr QFGCEI | 1 |  | Frozen Food | 15.125 | -10 | HG 2 Wire | 115 | 2.75 | 6.44 | 19.29 | 330 | 772.8 | 2314.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4QFGCEIFF |  | 4,4,4 | 12Dr QFGCEI | 1 |  | Frozen Food | 16.5 | -10 | HG 2 Wire | 115 | 3 | 6.96 | 21.06 | 360 | 835.2 | 2527.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3QFGCEIFF |  | 5,4,3 | 12Dr QFGCEI | 1 |  | Frozen Food | 16.5 | -10 | HG 2 Wire | 115 | 3 | 6.91 | 20.88 | 360 | 829.2 | 2505.6 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4QFGCEIFF |  | 5,4,4 | 13Dr QFGCEI | 1 |  | Frozen Food | 17.875 | -10 | HG 2 Wire | 115 | 3.25 | 7.43 | 22.65 | 390 | 891.6 | 2718 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QFGCEIFF |  | 5,5,3 | 13Dr QFGCEI | 1 |  | Frozen Food | 17.875 | -10 | HG 2 Wire | 115 | 3.25 | 7.38 | 22.47 | 390 | 885.6 | 2696.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QFGCEIFF |  | 5,5,4 | 14Dr QFGCEI | 1 |  | Frozen Food | 19.25 | -10 | HG 2 Wire | 115 | 3.5 | 7.9 | 24.24 | 420 | 948 | 2908.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEIFF |  | 4,4,3,3 | 14Dr QFGCEI | 1 |  | Frozen Food | 19.25 | -10 | HG 2 Wire | 115 | 3.5 | 8.24 | 24.54 | 420 | 988.8 | 2944.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QFGCEIFF |  | 5,5,5 | 15Dr QFGCEI | 1 |  | Frozen Food | 20.625 | -10 | HG 2 Wire | 115 | 3.75 | 8.37 | 25.83 | 450 | 1004.4 | 3099.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEIFF |  | 4,4,4,3 | 15Dr QFGCEI | 1 |  | Frozen Food | 20.625 | -10 | HG 2 Wire | 115 | 3.75 | 8.76 | 26.31 | 450 | 1051.2 | 3157.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEIFF |  | 5,5,3,3 | 16Dr QFGCEI | 1 |  | Frozen Food | 22 | -10 | HG 2 Wire | 115 | 4 | 9.18 | 27.72 | 480 | 1101.6 | 3326.4 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEIFF |  | 4,4,4,4 | 16Dr QFGCEI | 1 |  | Frozen Food | 22 | -10 | HG 2 Wire | 115 | 4 | 9.28 | 28.08 | 480 | 1113.6 | 3369.6 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,3,2QFGCEIFF | * | 4,3,2 | 9Dr QFGCEI | 1 |  | Frozen Food | 12.375 | -10 | HG 2 Wire | 115 | 2.25 | 5.51 | 15.9 | 270 | 661.2 | 1908 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEIFF | * | 5,3,2 | 10Dr QFGCEI | 1 |  | Frozen Food | 13.75 | -10 | HG 2 Wire | 115 | 2.5 | 5.98 | 17.49 | 300 | 717.6 | 2098.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEIFF |  | 5,3,3,3 | 14Dr QFGCEI | 1 |  | Frozen Food | 19.25 | -10 | HG 2 Wire | 115 | 3.5 | 8.19 | 24.36 | 420 | 982.8 | 2923.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEIFF |  | 4,4,3,2 | 13Dr QFGCEI | 1 |  | Frozen Food | 17.875 | -10 | HG 2 Wire | 115 | 3.25 | 7.83 | 22.92 | 390 | 939.6 | 2750.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QFGCEI | ICE CREAM | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEIIC |  | 2 | QFGCEI | 1 |  | Ice Cream | 2.85 | -17 | HG 2 Wire | 115 | 0.5 | 1.39 | 3.63 | 60 | 166.8 | 435.6 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEIIC |  | 3 | QFGCEI | 1 |  | Ice Cream | 4.275 | -17 | HG 2 Wire | 115 | 0.75 | 1.8 | 5.25 | 90 | 216 | 630 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEIIC |  | 4 | QFGCEI | 1 |  | Ice Cream | 5.7 | -17 | HG 2 Wire | 115 | 1 | 2.32 | 7.02 | 120 | 278.4 | 842.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEIIC |  | 5 | QFGCEI | 1 |  | Ice Cream | 7.125 | -17 | HG 2 Wire | 115 | 1.25 | 2.79 | 8.61 | 150 | 334.8 | 1033.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEIIC |  | 3,3 | 6Dr QFGCEI | 1 |  | Ice Cream | 8.55 | -17 | HG 2 Wire | 115 | 1.5 | 3.6 | 10.5 | 180 | 432 | 1260 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEIIC |  | 4,3 | 7Dr QFGCEI | 1 |  | Ice Cream | 9.975 | -17 | HG 2 Wire | 115 | 1.75 | 4.12 | 12.27 | 210 | 494.4 | 1472.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEIIC |  | 4,4 | 8Dr QFGCEI | 1 |  | Ice Cream | 11.4 | -17 | HG 2 Wire | 115 | 2 | 4.64 | 14.04 | 240 | 556.8 | 1684.8 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEIIC |  | 5,3 | 8Dr QFGCEI | 1 |  | Ice Cream | 11.4 | -17 | HG 2 Wire | 115 | 2 | 4.59 | 13.86 | 240 | 550.8 | 1663.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEIIC |  | 5,4 | 9Dr QFGCEI | 1 |  | Ice Cream | 12.825 | -17 | HG 2 Wire | 115 | 2.25 | 5.11 | 15.63 | 270 | 613.2 | 1875.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEIIC |  | 3,3,3 | 9Dr QFGCEI | 1 |  | Ice Cream | 12.825 | -17 | HG 2 Wire | 115 | 2.25 | 5.4 | 15.75 | 270 | 648 | 1890 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEIIC |  | 5,5 | 10Dr QFGCEI | 1 |  | Ice Cream | 14.25 | -17 | HG 2 Wire | 115 | 2.5 | 5.58 | 17.22 | 300 | 669.6 | 2066.4 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,3,3QFGCEIIC |  | 4,3,3 | 10Dr QFGCEI | 1 |  | Ice Cream | 14.25 | -17 | HG 2 Wire | 115 | 2.5 | 5.92 | 17.52 | 300 | 710.4 | 2102.4 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3,3QFGCEIIC |  | 5,3,3 | 11Dr QFGCEI | 1 |  | Ice Cream | 15.675 | -17 | HG 2 Wire | 115 | 2.75 | 6.39 | 19.11 | 330 | 766.8 | 2293.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3QFGCEIIC |  | 4,4,3 | 11Dr QFGCEI | 1 |  | Ice Cream | 15.675 | -17 | HG 2 Wire | 115 | 2.75 | 6.44 | 19.29 | 330 | 772.8 | 2314.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4QFGCEIIC |  | 4,4,4 | 12Dr QFGCEI | 1 |  | Ice Cream | 17.1 | -17 | HG 2 Wire | 115 | 3 | 6.96 | 21.06 | 360 | 835.2 | 2527.2 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3QFGCEIIC |  | 5,4,3 | 12Dr QFGCEI | 1 |  | Ice Cream | 17.1 | -17 | HG 2 Wire | 115 | 3 | 6.91 | 20.88 | 360 | 829.2 | 2505.6 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4QFGCEIIC |  | 5,4,4 | 13Dr QFGCEI | 1 |  | Ice Cream | 18.525 | -17 | HG 2 Wire | 115 | 3.25 | 7.43 | 22.65 | 390 | 891.6 | 2718 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QFGCEIIC |  | 5,5,3 | 13Dr QFGCEI | 1 |  | Ice Cream | 18.525 | -17 | HG 2 Wire | 115 | 3.25 | 7.38 | 22.47 | 390 | 885.6 | 2696.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QFGCEIIC |  | 5,5,4 | 14Dr QFGCEI | 1 |  | Ice Cream | 19.95 | -17 | HG 2 Wire | 115 | 3.5 | 7.9 | 24.24 | 420 | 948 | 2908.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEIIC |  | 4,4,3,3 | 14Dr QFGCEI | 1 |  | Ice Cream | 19.95 | -17 | HG 2 Wire | 115 | 3.5 | 8.24 | 24.54 | 420 | 988.8 | 2944.8 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QFGCEIIC |  | 5,5,5 | 15Dr QFGCEI | 1 |  | Ice Cream | 21.375 | -17 | HG 2 Wire | 115 | 3.75 | 8.37 | 25.83 | 450 | 1004.4 | 3099.6 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEIIC |  | 4,4,4,3 | 15Dr QFGCEI | 1 |  | Ice Cream | 21.375 | -17 | HG 2 Wire | 115 | 3.75 | 8.76 | 26.31 | 450 | 1051.2 | 3157.2 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEIIC |  | 5,5,3,3 | 16Dr QFGCEI | 1 |  | Ice Cream | 22.8 | -17 | HG 2 Wire | 115 | 4 | 9.18 | 27.72 | 480 | 1101.6 | 3326.4 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEIIC |  | 4,4,4,4 | 16Dr QFGCEI | 1 |  | Ice Cream | 22.8 | -17 | HG 2 Wire | 115 | 4 | 9.28 | 28.08 | 480 | 1113.6 | 3369.6 | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,3,2QFGCEIIC | * | 4,3,2 | 9Dr QFGCEI | 1 |  | Ice Cream | 12.825 | -17 | HG 2 Wire | 115 | 2.25 | 5.51 | 15.9 | 270 | 661.2 | 1908 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEIIC | * | 5,3,2 | 10Dr QFGCEI | 1 |  | Ice Cream | 14.25 | -17 | HG 2 Wire | 115 | 2.5 | 5.98 | 17.49 | 300 | 717.6 | 2098.8 | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEIIC |  | 5,3,3,3 | 14Dr QFGCEI | 1 |  | Ice Cream | 19.95 | -17 | HG 2 Wire | 115 | 3.5 | 8.19 | 24.36 | 420 | 982.8 | 2923.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEIIC |  | 4,4,3,2 | 13Dr QFGCEI | 1 |  | Ice Cream | 18.525 | -17 | HG 2 Wire | 115 | 3.25 | 7.83 | 22.92 | 390 | 939.6 | 2750.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | QFGCEID | FROZEN FOOD BACK TO BACK | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEIDFF |  | 2 | QFGCEID | 1 |  | Frozen Food | 2.1 | -10 | HG 2 Wire | 115 | 0.5 | 1.39 | 1.97 | 60 | 166.8 | 236.4 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEIDFF |  | 3 | QFGCEID | 1 |  | Frozen Food | 3.15 | -10 | HG 2 Wire | 115 | 0.75 | 1.8 | 2.81 | 90 | 216 | 337.2 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEIDFF |  | 4 | QFGCEID | 1 |  | Frozen Food | 4.2 | -10 | HG 2 Wire | 115 | 1 | 2.32 | 3.6 | 120 | 278.4 | 432 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEIDFF |  | 5 | QFGCEID | 1 |  | Frozen Food | 5.25 | -10 | HG 2 Wire | 115 | 1.25 | 2.79 | 4.45 | 150 | 334.8 | 534 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEIDFF |  | 3,3 | 6Dr QFGCEID | 1 |  | Frozen Food | 6.3 | -10 | HG 2 Wire | 115 | 1.5 | 3.6 | 5.62 | 180 | 432 | 674.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEIDFF |  | 4,3 | 7Dr QFGCEID | 1 |  | Frozen Food | 7.35 | -10 | HG 2 Wire | 115 | 1.75 | 4.12 | 6.41 | 210 | 494.4 | 769.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEIDFF |  | 4,4 | 8Dr QFGCEID | 1 |  | Frozen Food | 8.4 | -10 | HG 2 Wire | 115 | 2 | 4.64 | 7.2 | 240 | 556.8 | 864 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEIDFF |  | 5,3 | 8Dr QFGCEID | 1 |  | Frozen Food | 8.4 | -10 | HG 2 Wire | 115 | 2 | 4.59 | 7.26 | 240 | 550.8 | 871.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEIDFF |  | 5,4 | 9Dr QFGCEID | 1 |  | Frozen Food | 9.45 | -10 | HG 2 Wire | 115 | 2.25 | 5.11 | 8.05 | 270 | 613.2 | 966 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEIDFF |  | 3,3,3 | 9Dr QFGCEID | 1 |  | Frozen Food | 9.45 | -10 | HG 2 Wire | 115 | 2.25 | 5.4 | 8.43 | 270 | 648 | 1011.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEIDFF |  | 5,5 | 10Dr QFGCEID | 1 |  | Frozen Food | 10.5 | -10 | HG 2 Wire | 115 | 2.5 | 5.58 | 8.9 | 300 | 669.6 | 1068 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QFGCEIDFF |  | 4,3,3 | 10Dr QFGCEID | 1 |  | Frozen Food | 10.5 | -10 | HG 2 Wire | 115 | 2.5 | 5.92 | 9.22 | 300 | 710.4 | 1106.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QFGCEIDFF |  | 5,3,3 | 11Dr QFGCEID | 1 |  | Frozen Food | 11.55 | -10 | HG 2 Wire | 115 | 2.75 | 6.39 | 10.07 | 330 | 766.8 | 1208.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,3QFGCEIDFF |  | 4,4,3 | 11Dr QFGCEID | 1 |  | Frozen Food | 11.55 | -10 | HG 2 Wire | 115 | 2.75 | 6.44 | 10.01 | 330 | 772.8 | 1201.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,4QFGCEIDFF |  | 4,4,4 | 12Dr QFGCEID | 1 |  | Frozen Food | 12.6 | -10 | HG 2 Wire | 115 | 3 | 6.96 | 10.8 | 360 | 835.2 | 1296 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,3QFGCEIDFF |  | 5,4,3 | 12Dr QFGCEID | 1 |  | Frozen Food | 12.6 | -10 | HG 2 Wire | 115 | 3 | 6.91 | 10.86 | 360 | 829.2 | 1303.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,4QFGCEIDFF |  | 5,4,4 | 13Dr QFGCEID | 1 |  | Frozen Food | 13.65 | -10 | HG 2 Wire | 115 | 3.25 | 7.43 | 11.65 | 390 | 891.6 | 1398 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5,3QFGCEIDFF |  | 5,5,3 | 13Dr QFGCEID | 1 |  | Frozen Food | 13.65 | -10 | HG 2 Wire | 115 | 3.25 | 7.38 | 11.71 | 390 | 885.6 | 1405.2 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5,4QFGCEIDFF |  | 5,5,4 | 14Dr QFGCEID | 1 |  | Frozen Food | 14.7 | -10 | HG 2 Wire | 115 | 3.5 | 7.9 | 12.5 | 420 | 948 | 1500 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEIDFF |  | 4,4,3,3 | 14Dr QFGCEID | 1 |  | Frozen Food | 14.7 | -10 | HG 2 Wire | 115 | 3.5 | 8.24 | 12.82 | 420 | 988.8 | 1538.4 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5,5QFGCEIDFF |  | 5,5,5 | 15Dr QFGCEID | 1 |  | Frozen Food | 15.75 | -10 | HG 2 Wire | 115 | 3.75 | 8.37 | 13.35 | 450 | 1004.4 | 1602 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEIDFF |  | 4,4,4,3 | 15Dr QFGCEID | 1 |  | Frozen Food | 15.75 | -10 | HG 2 Wire | 115 | 3.75 | 8.76 | 13.61 | 450 | 1051.2 | 1633.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEIDFF |  | 5,5,3,3 | 16Dr QFGCEID | 1 |  | Frozen Food | 16.8 | -10 | HG 2 Wire | 115 | 4 | 9.18 | 14.52 | 480 | 1101.6 | 1742.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEIDFF |  | 4,4,4,4 | 16Dr QFGCEID | 1 |  | Frozen Food | 16.8 | -10 | HG 2 Wire | 115 | 4 | 9.28 | 14.4 | 480 | 1113.6 | 1728 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,2QFGCEIDFF | * | 4,3,2 | 9Dr QFGCEID | 1 |  | Frozen Food | 9.45 | -10 | HG 2 Wire | 115 | 2.25 | 5.51 | 8.38 | 270 | 661.2 | 1005.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEIDFF | * | 5,3,2 | 10Dr QFGCEID | 1 |  | Frozen Food | 10.5 | -10 | HG 2 Wire | 115 | 2.5 | 5.98 | 9.23 | 300 | 717.6 | 1107.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEIDFF |  | 5,3,3,3 | 14Dr QFGCEID | 1 |  | Frozen Food | 14.7 | -10 | HG 2 Wire | 115 | 3.5 | 8.19 | 12.88 | 420 | 982.8 | 1545.6 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEIDFF |  | 4,4,3,2 | 13Dr QFGCEID | 1 |  | Frozen Food | 13.65 | -10 | HG 2 Wire | 115 | 3.25 | 7.83 | 11.98 | 390 | 939.6 | 1437.6 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
|  | QFGCEID | ICE CREAM BACK TO BACK | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2QFGCEIDIC |  | 2 | QFGCEID | 1 |  | Ice Cream | 2.2 | -17 | HG 2 Wire | 115 | 0.5 | 1.39 | 1.97 | 60 | 166.8 | 236.4 | E14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3QFGCEIDIC |  | 3 | QFGCEID | 1 |  | Ice Cream | 3.3 | -17 | HG 2 Wire | 115 | 0.75 | 1.8 | 2.81 | 90 | 216 | 337.2 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4QFGCEIDIC |  | 4 | QFGCEID | 1 |  | Ice Cream | 4.4 | -17 | HG 2 Wire | 115 | 1 | 2.32 | 3.6 | 120 | 278.4 | 432 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5QFGCEIDIC |  | 5 | QFGCEID | 1 |  | Ice Cream | 5.5 | -17 | HG 2 Wire | 115 | 1.25 | 2.79 | 4.45 | 150 | 334.8 | 534 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3QFGCEIDIC |  | 3,3 | 6Dr QFGCEID | 1 |  | Ice Cream | 6.6 | -17 | HG 2 Wire | 115 | 1.5 | 3.6 | 5.62 | 180 | 432 | 674.4 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3QFGCEIIC |  | 4,3 | 7Dr QFGCEID | 1 |  | Ice Cream | 7.7 | -17 | HG 2 Wire | 115 | 1.75 | 4.12 | 6.41 | 210 | 494.4 | 769.2 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4QFGCEIIC |  | 4,4 | 8Dr QFGCEID | 1 |  | Ice Cream | 8.8 | -17 | HG 2 Wire | 115 | 2 | 4.64 | 7.2 | 240 | 556.8 | 864 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3QFGCEIIC |  | 5,3 | 8Dr QFGCEID | 1 |  | Ice Cream | 8.8 | -17 | HG 2 Wire | 115 | 2 | 4.59 | 7.26 | 240 | 550.8 | 871.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4QFGCEIIC |  | 5,4 | 9Dr QFGCEID | 1 |  | Ice Cream | 9.9 | -17 | HG 2 Wire | 115 | 2.25 | 5.11 | 8.05 | 270 | 613.2 | 966 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3QFGCEIIC |  | 3,3,3 | 9Dr QFGCEID | 1 |  | Ice Cream | 9.9 | -17 | HG 2 Wire | 115 | 2.25 | 5.4 | 8.43 | 270 | 648 | 1011.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5QFGCEIIC |  | 5,5 | 10Dr QFGCEID | 1 |  | Ice Cream | 11 | -17 | HG 2 Wire | 115 | 2.5 | 5.58 | 8.9 | 300 | 669.6 | 1068 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3QFGCEIIC |  | 4,3,3 | 10Dr QFGCEID | 1 |  | Ice Cream | 11 | -17 | HG 2 Wire | 115 | 2.5 | 5.92 | 9.22 | 300 | 710.4 | 1106.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3QFGCEIIC |  | 5,3,3 | 11Dr QFGCEID | 1 |  | Ice Cream | 12.1 | -17 | HG 2 Wire | 115 | 2.75 | 6.39 | 10.07 | 330 | 766.8 | 1208.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,3QFGCEIIC |  | 4,4,3 | 11Dr QFGCEID | 1 |  | Ice Cream | 12.1 | -17 | HG 2 Wire | 115 | 2.75 | 6.44 | 10.01 | 330 | 772.8 | 1201.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4,4QFGCEIIC |  | 4,4,4 | 12Dr QFGCEID | 1 |  | Ice Cream | 13.2 | -17 | HG 2 Wire | 115 | 3 | 6.96 | 10.8 | 360 | 835.2 | 1296 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,3QFGCEIIC |  | 5,4,3 | 12Dr QFGCEID | 1 |  | Ice Cream | 13.2 | -17 | HG 2 Wire | 115 | 3 | 6.91 | 10.86 | 360 | 829.2 | 1303.2 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4,4QFGCEIIC |  | 5,4,4 | 13Dr QFGCEID | 1 |  | Ice Cream | 14.3 | -17 | HG 2 Wire | 115 | 3.25 | 7.43 | 11.65 | 390 | 891.6 | 1398 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3QFGCEIIC |  | 5,5,3 | 13Dr QFGCEID | 1 |  | Ice Cream | 14.3 | -17 | HG 2 Wire | 115 | 3.25 | 7.38 | 11.71 | 390 | 885.6 | 1405.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4QFGCEIIC |  | 5,5,4 | 14Dr QFGCEID | 1 |  | Ice Cream | 15.4 | -17 | HG 2 Wire | 115 | 3.5 | 7.9 | 12.5 | 420 | 948 | 1500 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3QFGCEIIC |  | 4,4,3,3 | 14Dr QFGCEID | 1 |  | Ice Cream | 15.4 | -17 | HG 2 Wire | 115 | 3.5 | 8.24 | 12.82 | 420 | 988.8 | 1538.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5QFGCEIIC |  | 5,5,5 | 15Dr QFGCEID | 1 |  | Ice Cream | 16.5 | -17 | HG 2 Wire | 115 | 3.75 | 8.37 | 13.35 | 450 | 1004.4 | 1602 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3QFGCEIIC |  | 4,4,4,3 | 15Dr QFGCEID | 1 |  | Ice Cream | 16.5 | -17 | HG 2 Wire | 115 | 3.75 | 8.76 | 13.61 | 450 | 1051.2 | 1633.2 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3QFGCEIIC |  | 5,5,3,3 | 16Dr QFGCEID | 1 |  | Ice Cream | 17.6 | -17 | HG 2 Wire | 115 | 4 | 9.18 | 14.52 | 480 | 1101.6 | 1742.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,4QFGCEIIC |  | 4,4,4,4 | 16Dr QFGCEID | 1 |  | Ice Cream | 17.6 | -17 | HG 2 Wire | 115 | 4 | 9.28 | 14.4 | 480 | 1113.6 | 1728 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,2QFGCEIIC | * | 4,3,2 | 9Dr QFGCEID | 1 |  | Ice Cream | 9.9 | -17 | HG 2 Wire | 115 | 2.25 | 5.51 | 8.38 | 270 | 661.2 | 1005.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,2QFGCEIIC | * | 5,3,2 | 10Dr QFGCEID | 1 |  | Ice Cream | 11 | -17 | HG 2 Wire | 115 | 2.5 | 5.98 | 9.23 | 300 | 717.6 | 1107.6 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3,3QFGCEIIC |  | 5,3,3,3 | 14Dr QFGCEID | 1 |  | Ice Cream | 15.4 | -17 | HG 2 Wire | 115 | 3.5 | 8.19 | 12.88 | 420 | 982.8 | 1545.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2QFGCEIIC |  | 4,4,3,2 | 13Dr QFGCEID | 1 |  | Ice Cream | 14.3 | -17 | HG 2 Wire | 115 | 3.25 | 7.83 | 11.98 | 390 | 939.6 | 1437.6 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | D6NL1 | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8D6NL1 |  | 8' | D6NL1 |  |  | Dairy | 11.6 | 20 | Off Cycle | 115 | 1.06 | 0.92 |  | 127.2 | 110.4 |  |  |  | SORIT 12 |  |  | 5/8 | 1/2
12D6NL1 |  | 12' | D6NL1 |  |  | Dairy | 17.4 | 20 | Off Cycle | 115 | 1.59 | 1.48 |  | 190.8 | 177.6 |  |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'8D6NL1 |  | 8'8' | 16' D6NL1 |  |  | Dairy | 23.2 | 20 | Off Cycle | 115 | 2.12 | 1.84 |  | 254.4 | 220.8 |  |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'12D6NL1 |  | 8'12' | 20' D6NL1 |  |  | Dairy | 29 | 20 | Off Cycle | 115 | 2.65 | 2.4 |  | 318 | 288 |  |  |  | SORIT 12 |  |  | 1 1/8 | 1/2
8'8'8D6NL1 |  | 8'8'8' | 24' D6NL1 |  |  | Dairy | 34.8 | 20 | Off Cycle | 115 | 3.18 | 2.76 |  | 381.6 | 331.2 |  |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
12'12D6NL1 |  | 12'12' | 24' D6NL1 |  |  | Dairy | 34.8 | 20 | Off Cycle | 115 | 3.18 | 2.96 |  | 381.6 | 355.2 |  |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
8'8'12D6NL1 |  | 8'8'12' | 28' D6NL1 |  |  | Dairy | 40.6 | 20 | Off Cycle | 115 | 3.71 | 3.32 |  | 445.2 | 398.4 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8D6NL1 |  | 8'8'8'8' | 32' D6NL1 |  |  | Dairy | 46.4 | 20 | Off Cycle | 115 | 4.24 | 3.68 |  | 508.8 | 441.6 |  |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'12'12D6NL1 |  | 8'12'12' | 32' D6NL1 |  |  | Dairy | 46.4 | 20 | Off Cycle | 115 | 4.24 | 3.88 |  | 508.8 | 465.6 |  |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'12D6NL1 |  | 8'8'8'12' | 36' D6NL1 |  |  | Dairy | 52.2 | 20 | Off Cycle | 115 | 4.77 | 1 |  | 572.4 | 120 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
12'12'12D6NL1 |  | 12'12'12' | 36' D6NL1 |  |  | Dairy | 52.2 | 20 | Off Cycle | 115 | 4.77 | 4.44 |  | 572.4 | 532.8 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'8D6NL1 |  | 8'8'8'8'8' | 40' D6NL1 |  |  | Beverage | 58 | 20 | Off Cycle | 115 | 5.3 | 4.6 |  | 636 | 552 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'12'12D6NL1 |  | 8'8'12'12' | 40' D6NL1 |  |  | Beverage | 58 | 20 | Off Cycle | 115 | 5.3 | 4.8 |  | 636 | 576 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'12D6NL1 |  | 8'8'8'8'12' | 44' D6NL1 |  |  | Beverage | 63.8 | 20 | Off Cycle | 115 | 5.83 | 5.16 |  | 699.6 | 619.2 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'12'12'12D6NL1 |  | 8'12'12'12' | 44' D6NL1 |  |  | Beverage | 63.8 | 20 | Off Cycle | 115 | 5.83 | 5.36 |  | 699.6 | 643.2 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'12'12D6NL1 |  | 8'8'8'12'12' | 48' D6NL1 |  |  | Beverage | 69.6 | 20 | Off Cycle | 115 | 6.36 | 5.72 |  | 763.2 | 686.4 | [6 empty] | 1 5/8 | 5/8
12'12'12'12D6NL1 |  | 12'12'12'12' | 48' D6NL1 |  |  | Beverage | 69.6 | 20 | Off Cycle | 115 | 6.36 | 5.92 |  | 763.2 | 710.4 | [6 empty] | 1 5/8 | 5/8
|  | D6L1 (DAIRY) | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8D6L1D |  | 8' | D6L1 |  |  | Dairy | 10.72 | 20 | Off Cycle | 115 | 1.64 | 2.1 |  | 196.8 | 252 |  |  |  | SORIT 12 |  |  | 5/8 | 1/2
12D6L1D |  | 12' | D6L1 |  |  | Dairy | 16.08 | 20 | Off Cycle | 115 | 2.46 | 3.2 |  | 295.2 | 384 |  |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'8D6L1D |  | 8'8' | 16' D6L1 |  |  | Dairy | 21.44 | 20 | Off Cycle | 115 | 3.28 | 4.2 |  | 393.6 | 504 |  |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'12D6L1D |  | 8'12' | 20' D6L1 |  |  | Dairy | 26.8 | 20 | Off Cycle | 115 | 4.1 | 5.3 |  | 492 | 636 |  |  |  | SORIT 12 |  |  | 1 1/8 | 1/2
8'8'8D6L1D |  | 8'8'8' | 24' D6L1 |  |  | Dairy | 32.16 | 20 | Off Cycle | 115 | 4.92 | 6.3 |  | 590.4 | 756 |  |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
12'12D6L1D |  | 12'12' | 24' D6L1 |  |  | Dairy | 32.16 | 20 | Off Cycle | 115 | 4.92 | 6.4 |  | 590.4 | 768 |  |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
8'8'12D6L1D |  | 8'8'12' | 28' D6L1 |  |  | Dairy | 37.52 | 20 | Off Cycle | 115 | 5.74 | 7.4 |  | 688.8 | 888 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8D6L1D |  | 8'8'8'8' | 32' D6L1 |  |  | Dairy | 42.88 | 20 | Off Cycle | 115 | 6.56 | 8.4 |  | 787.2 | 1008 |  |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'12'12D6L1D |  | 8'12'12' | 32' D6L1 |  |  | Dairy | 42.88 | 20 | Off Cycle | 115 | 6.56 | 8.5 |  | 787.2 | 1020 |  |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'12D6L1D |  | 8'8'8'12' | 36' D6L1 |  |  | Dairy | 48.24 | 20 | Off Cycle | 115 | 7.38 | 9.5 |  | 885.6 | 1140 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
12'12'12D6L1D |  | 12'12'12' | 36' D6L1 |  |  | Dairy | 48.24 | 20 | Off Cycle | 115 | 7.38 | 9.6 |  | 885.6 | 1152 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'8D6L1D |  | 8'8'8'8'8' | 40' D6L1 |  |  | Dairy | 53.6 | 20 | Off Cycle | 115 | 8.2 | 10.5 |  | 984 | 1260 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'12'12D6L1D |  | 8'8'12'12' | 40' D6L1 |  |  | Dairy | 53.6 | 20 | Off Cycle | 115 | 8.2 | 10.6 |  | 984 | 1272 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'12D6L1D |  | 8'8'8'8'12' | 44' D6L1 |  |  | Dairy | 58.96 | 20 | Off Cycle | 115 | 9.02 | 11.6 |  | 1082.4 | 1392 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'12'12'12D6L1D |  | 8'12'12'12' | 44' D6L1 |  |  | Dairy | 58.96 | 20 | Off Cycle | 115 | 9.02 | 11.7 |  | 1082.4 | 1404 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'12'12D6L1D |  | 8'8'8'12'12' | 48' D6L1 |  |  | Dairy | 64.32 | 20 | Off Cycle | 115 | 9.84 | 12.7 |  | 1180.8 | 1524 | [6 empty] | 1 5/8 | 5/8
12'12'12'12D6L1D |  | 12'12'12'12' | 48' D6L1 |  |  | Dairy | 64.32 | 20 | Off Cycle | 115 | 9.84 | 12.8 |  | 1180.8 | 1536 | [6 empty] | 1 5/8 | 5/8
D6L1 DELI MEAT
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8D6L1DM |  | 8' | D6L1 | 1 |  | Deli Meat | 12 | 20 | HG 2 Wire | 115 | 0.64 | 0.92 |  | 76.8 | 110.4 |  | E14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
12D6L1DM |  | 12' | D6L1 | 1 |  | Deli Meat | 18 | 20 | HG 2 Wire | 115 | 0.96 | 1.48 |  | 115.2 | 177.6 |  | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8D6L1DM |  | 8'8' | 16' D6L1 | 1 |  | Deli Meat | 24 | 20 | Off Cycle | 115 | 1.28 | 1.84 |  | 153.6 | 220.8 |  | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'12D6L1DM |  | 8'12' | 20' D6L1 | 1 |  | Deli Meat | 30 | 20 | Off Cycle | 115 | 1.6 | 2.4 |  | 192 | 288 |  | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8D6L1DM |  | 8'8'8' | 24' D6L1 | 1 |  | Deli Meat | 36 | 20 | Off Cycle | 115 | 1.92 | 2.76 |  | 230.4 | 331.2 |  | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12D6L1DM |  | 12'12' | 24' D6L1 | 1 |  | Deli Meat | 36 | 20 | Off Cycle | 115 | 1.92 | 2.96 |  | 230.4 | 355.2 |  | E14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12D6L1DM |  | 8'8'12' | 28' D6L1 | 1 |  | Deli Meat | 42 | 20 | Off Cycle | 115 | 2.24 | 3.32 |  | 268.8 | 398.4 |  | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'8D6L1DM |  | 8'8'8'8' | 32' D6L1 | 1 |  | Deli Meat | 48 | 20 | Off Cycle | 115 | 2.56 | 3.68 |  | 307.2 | 441.6 |  | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'12'12D6L1DM |  | 8'12'12' | 32' D6L1 | 1 |  | Deli Meat | 48 | 20 | Off Cycle | 115 | 2.56 | 3.88 |  | 307.2 | 465.6 |  | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'12D6L1DM |  | 8'8'8'12' | 36' D6L1 | 1 |  | Deli Meat | 54 | 20 | Off Cycle | 115 | 2.88 | 4.24 |  | 345.6 | 508.8 |  | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
12'12'12D6L1DM |  | 12'12'12' | 36' D6L1 | 1 |  | Deli Meat | 54 | 20 | Off Cycle | 115 | 2.88 | 4.44 |  | 345.6 | 532.8 |  | E14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'8D6L1DM |  | 8'8'8'8'8' | 40' D6L1 | 1 |  | Deli Meat | 60 | 20 | Off Cycle | 115 | 3.2 | 4.6 |  | 384 | 552 |  | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 7/8
8'8'12'12D6L1DM |  | 8'8'12'12' | 40' D6L1 | 1 |  | Deli Meat | 60 | 20 | Off Cycle | 115 | 3.2 | 4.8 |  | 384 | 576 |  | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 7/8
8'8'8'8'12D6L1DM |  | 8'8'8'8'12' | 44' D6L1 | 1 |  | Deli Meat | 66 | 20 | Off Cycle | 115 | 3.52 | 5.16 |  | 422.4 | 619.2 |  | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 7/8
8'12'12'12D6L1DM |  | 8'12'12'12' | 44' D6L1 | 1 |  | Deli Meat | 66 | 20 | Off Cycle | 115 | 3.52 | 5.36 |  | 422.4 | 643.2 |  | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 7/8
8'8'8'12'12D6L1DM |  | 8'8'8'12'12' | 48' D6L1 | 1 |  | Deli Meat | 72 | 20 | Off Cycle | 115 | 3.84 | 5.72 |  | 460.8 | 686.4 |  | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 7/8
12'12'12'12D6L1DM |  | 12'12'12'12' | 48' D6L1 | 1 |  | Deli Meat | 72 | 20 | Off Cycle | 115 | 3.84 | 5.92 |  | 460.8 | 710.4 |  | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 7/8
|  | D61 & D6 DAIRY (BEVERAGE, EGGS, & DAIRY) | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8D61D |  | 8' | D61 |  |  | Dairy | 10 | 20 | Off Cycle | 115 | 0.5 | 3.3 |  | 60 | 396 |  |  |  | SORIT 12 |  |  | 5/8 | 1/2
12D61D |  | 12' | D61 |  |  | Dairy | 15 | 20 | Off Cycle | 115 | 0.8 | 4.8 |  | 96 | 576 |  |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'8D61D |  | 8'8' | 16' D61 |  |  | Dairy | 20 | 20 | Off Cycle | 115 | 1 | 6.6 |  | 120 | 792 |  |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'12D61D |  | 8'12' | 20' D61 |  |  | Dairy | 25 | 20 | Off Cycle | 115 | 1.3 | 8.1 |  | 156 | 972 |  |  |  | SORIT 12 |  |  | 1 1/8 | 1/2
8'8'8D61D |  | 8'8'8' | 24' D61 |  |  | Dairy | 30 | 20 | Off Cycle | 115 | 1.5 | 9.9 |  | 180 | 1188 |  |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
12'12D61D |  | 12'12' | 24' D61 |  |  | Dairy | 30 | 20 | Off Cycle | 115 | 1.6 | 9.6 |  | 192 | 1152 |  |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
8'8'12D61D |  | 8'8'12' | 28' D61 |  |  | Dairy | 35 | 20 | Off Cycle | 115 | 1.8 | 11.4 |  | 216 | 1368 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8D61D |  | 8'8'8'8' | 32' D61 |  |  | Dairy | 40 | 20 | Off Cycle | 115 | 2 | 13.2 |  | 240 | 1584 |  |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'12'12D61D |  | 8'12'12' | 32' D61 |  |  | Dairy | 40 | 20 | Off Cycle | 115 | 2.1 | 12.9 |  | 252 | 1548 |  |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'12D61D |  | 8'8'8'12' | 36' D61 |  |  | Dairy | 45 | 20 | Off Cycle | 115 | 2.3 | 14.7 |  | 276 | 1764 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
12'12'12D61D |  | 12'12'12' | 36' D61 |  |  | Dairy | 45 | 20 | Off Cycle | 115 | 2.4 | 14.4 |  | 288 | 1728 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'8D61D |  | 8'8'8'8'8' | 40' D61 |  |  | Beverage | 50 | 20 | Off Cycle | 115 | 2.5 | 16.5 |  | 300 | 1980 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'12'12D61D |  | 8'8'12'12' | 40' D61 |  |  | Beverage | 50 | 20 | Off Cycle | 115 | 2.6 | 16.2 |  | 312 | 1944 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'12D61D |  | 8'8'8'8'12' | 44' D61 |  |  | Beverage | 55 | 20 | Off Cycle | 115 | 2.8 | 18 |  | 336 | 2160 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'12'12'12D61D |  | 8'12'12'12' | 44' D61 |  |  | Beverage | 55 | 20 | Off Cycle | 115 | 2.9 | 17.7 |  | 348 | 2124 |  |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'12'12D61D |  | 8'8'8'12'12' | 48' D61 |  |  | Beverage | 60 | 20 | Off Cycle | 115 | 3.1 | 19.5 |  | 372 | 2340 | [6 empty] | 1 5/8 | 5/8
12'12'12'12D61D |  | 12'12'12'12' | 48' D61 |  |  | Beverage | 60 | 20 | Off Cycle | 115 | 3.2 | 19.2 |  | 384 | 2304 | [6 empty] | 1 5/8 | 5/8
|  | D61 DELI MEAT ONLY | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8D61DM |  | 8' | D61 | 1 |  | Deli Meat | 10.68 | 15 | HG 2 Wire | 115 | 0.7 | 3.3 |  | 84 | 396 |  | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
12D61DM |  | 12' | D61 | 1 |  | Deli Meat | 16.02 | 15 | HG 2 Wire | 115 | 1 | 4.8 |  | 120 | 576 |  | ME14S250 |  | SORIT 12 |  |  | 7/8 | 1/2
8'8D61DM |  | 8'8' | 16' D61 | 1 |  | Deli Meat | 21.36 | 15 | HG 2 Wire | 115 | 1.4 | 6.6 |  | 168 | 792 |  | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'12D61DM |  | 8'12' | 20' D61 | 1 |  | Deli Meat | 26.7 | 15 | HG 2 Wire | 115 | 1.7 | 8.1 |  | 204 | 972 |  | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8D61DM |  | 8'8'8' | 24' D61 | 1 |  | Deli Meat | 32.04 | 15 | HG 2 Wire | 115 | 2.1 | 9.9 |  | 252 | 1188 |  | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12D61DM |  | 12'12' | 24' D61 | 1 |  | Deli Meat | 32.04 | 15 | HG 2 Wire | 115 | 2 | 9.6 |  | 240 | 1152 |  | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12D61DM |  | 8'8'12' | 28' D61 | 1 |  | Deli Meat | 37.38 | 15 | HG 2 Wire | 115 | 2.4 | 11.4 |  | 288 | 1368 |  | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'8D61DM |  | 8'8'8'8' | 32' D61 | 1 |  | Deli Meat | 42.72 | 15 | HG 2 Wire | 115 | 2.8 | 13.2 |  | 336 | 1584 |  | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'12'12D61DM |  | 8'12'12' | 32' D61 | 1 |  | Deli Meat | 42.72 | 15 | HG 2 Wire | 115 | 2.7 | 12.9 |  | 324 | 1548 |  | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'12D61DM |  | 8'8'8'12' | 36' D61 | 1 |  | Deli Meat | 48.06 | 15 | HG 2 Wire | 115 | 3.1 | 14.7 |  | 372 | 1764 |  | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
12'12'12D61DM |  | 12'12'12' | 36' D61 | 1 |  | Deli Meat | 48.06 | 15 | HG 2 Wire | 115 | 3 | 14.4 |  | 360 | 1728 |  | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'8D61DM |  | 8'8'8'8'8' | 40' D61 | 1 |  | Deli Meat | 53.4 | 15 | HG 2 Wire | 115 | 3.5 | 16.5 |  | 420 | 1980 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'12'12D61DM |  | 8'8'12'12' | 40' D61 | 1 |  | Deli Meat | 53.4 | 15 | HG 2 Wire | 115 | 3.4 | 16.2 |  | 408 | 1944 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'8'8'12D61DM |  | 8'8'8'8'12' | 44' D61 | 1 |  | Deli Meat | 58.74 | 15 | HG 2 Wire | 115 | 3.8 | 18 |  | 456 | 2160 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'12'12'12D61DM |  | 8'12'12'12' | 44' D61 | 1 |  | Deli Meat | 58.74 | 15 | HG 2 Wire | 115 | 3.7 | 17.7 |  | 444 | 2124 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'8'12'12D61DM |  | 8'8'8'12'12' | 48' D61 | 1 |  | Deli Meat | 64.08 | 15 | HG 2 Wire | 115 | 4.1 | 19.5 |  | 492 | 2340 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
12'12'12'12D61DM |  | 12'12'12'12' | 48' D61 | 1 |  | Deli Meat | 64.08 | 15 | HG 2 Wire | 115 | 4 | 19.2 |  | 480 | 2304 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | D6 DELI MEAT ONLY | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8D6DM |  | 8' | D6 |  |  | Deli Meat* | 10.68 | 15 | HG 2 Wire | 115 | 1.7 | 3.4 |  | 204 | 408 |  | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
12D6DM |  | 12' | D6 |  |  | Deli Meat* | 16.02 | 15 | HG 2 Wire | 115 | 2.5 | 6.1 |  | 300 | 732 |  | ME14S250 |  | SORIT 12 |  |  | 7/8 | 1/2
8'8D6DM |  | 8'8' | 16' D6 |  |  | Deli Meat* | 21.36 | 15 | HG 2 Wire | 115 | 3.4 | 6.8 |  | 408 | 816 |  | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'12D6DM |  | 8'12' | 20' D6 |  |  | Deli Meat* | 26.7 | 15 | HG 2 Wire | 115 | 4.2 | 9.5 |  | 504 | 1140 |  | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8D6DM |  | 8'8'8' | 24' D6 |  |  | Deli Meat* | 32.04 | 15 | HG 2 Wire | 115 | 5.1 | 10.2 |  | 612 | 1224 |  | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12D6DM |  | 12'12' | 24' D6 |  |  | Deli Meat* | 32.04 | 15 | HG 2 Wire | 115 | 5 | 12.2 |  | 600 | 1464 |  | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12D6DM |  | 8'8'12' | 28' D6 |  |  | Deli Meat* | 37.38 | 15 | HG 2 Wire | 115 | 5.9 | 12.9 |  | 708 | 1548 |  | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'8D6DM |  | 8'8'8'8' | 32' D6 |  |  | Deli Meat* | 42.72 | 15 | HG 2 Wire | 115 | 6.8 | 13.6 |  | 816 | 1632 |  | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'12'12D6DM |  | 8'12'12' | 32' D6 |  |  | Deli Meat* | 42.72 | 15 | HG 2 Wire | 115 | 6.7 | 15.6 |  | 804 | 1872 |  | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'12D6DM |  | 8'8'8'12' | 36' D6 |  |  | Deli Meat* | 48.06 | 15 | HG 2 Wire | 115 | 7.6 | 16.3 |  | 912 | 1956 |  | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
12'12'12D6DM |  | 12'12'12' | 36' D6 |  |  | Deli Meat* | 48.06 | 15 | HG 2 Wire | 115 | 7.5 | 18.3 |  | 900 | 2196 |  | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'8'8D6DM |  | 8'8'8'8'8' | 40' D6 |  |  | Deli Meat* | 53.4 | 15 | HG 2 Wire | 115 | 8.5 | 17 |  | 1020 | 2040 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'12'12D6DM |  | 8'8'12'12' | 40' D6 |  |  | Deli Meat* | 53.4 | 15 | HG 2 Wire | 115 | 8.4 | 19 |  | 1008 | 2280 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'8'8'12D6DM |  | 8'8'8'8'12' | 44' D6 |  |  | Deli Meat* | 58.74 | 15 | HG 2 Wire | 115 | 9.3 | 19.7 |  | 1116 | 2364 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'12'12'12D6DM |  | 8'12'12'12' | 44' D6 |  |  | Deli Meat* | 58.74 | 15 | HG 2 Wire | 115 | 9.2 | 21.7 |  | 1104 | 2604 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'8'12'12D6DM |  | 8'8'8'12'12' | 48' D6 |  |  | Deli Meat* | 64.08 | 15 | HG 2 Wire | 115 | 10.1 | 22.4 |  | 1212 | 2688 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
12'12'12'12D6DM |  | 12'12'12'12' | 48' D6 |  |  | Deli Meat* | 64.08 | 15 | HG 2 Wire | 115 | 10 | 24.4 |  | 1200 | 2928 |  | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | DELI CASES | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8S1AG |  | 8' | S1AG |  |  | Self Serve Deli | 4.16 | 15 | HG 2 Wire | 115 | 0.8 |  | 0.7 | 96 | 0 | 84 | ME14S250 |  | SORIT 12 |  | 7/8 | 5/8 | 5/8
12S1AG |  | 12' | S1AG |  |  | Self Serve Deli | 6.24 | 15 | HG 2 Wire | 115 | 1.7 |  | 1.3 | 204 | 0 | 156 | ME14S250 |  | SORIT 12 |  | 7/8 | 5/8 | 5/8
5LD11 |  | 5' | LD11 | 1 |  | Dual Temp Promo | 3.35 | -25 | Elec.10.8A | 115 | 0.3 |  | 1.6 | 36 | 0 | 192 |  | Ball Valve | Ball Valve
8S39S1 |  | 8' | S39S1 |  |  | Cold Deli | 2.56 | 20 | Off Cycle | 115 |  | 2.1 |  | 0 | 252 | 0 |  |  | SORIT 12 |  | 5/8 | 1/2 | 1/2
12S39S1 |  | 12' | S39S1 |  |  | Cold Deli | 3.84 | 20 | Off Cycle | 115 |  | 2.6 |  | 0 | 312 | 0 |  |  | SORIT 12 |  | 5/8 | 1/2 | 1/2
16S39S1 |  | 8'8' | 16' S39S1 |  |  | Cold Deli | 5.12 | 20 | Off Cycle | 115 | 0 | 4.2 | 0 | 0 | 504 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
8S39VL1 |  | 8' | S39VL1 |  |  | Cold Deli | 3.4 | 20 | Off Cycle | 115 |  | 2.1 |  | 0 | 252 | 0 |  |  | SORIT 12
8'8S39VL1 |  | 8'8' | 16' S39VL1 |  |  | Cold Deli | 6.8 | 20 | Off Cycle | 115 |  | 4.2 |  | 0 | 504 | 0 |  |  | SORIT 12
12S39VL1 |  | 12' | S39VL1 |  |  | Cold Deli | 5.1 | 20 | Off Cycle | 115 |  | 2.6 |  | 0 | 312 | 0 |  |  | SORIT 12
6L5FA1 |  | 6' | L5FA1 | 1 |  | Frozen Food | 8 | -25 | HG 2 Wire | 115 | 4.1 | 2.1 | 5.1 | 492 | 252 | 612 | ME14S250 |  | ME19S270 |  | 1 1/8 | 7/8
6B4V1 |  | 6' | B4V1 |  |  | Refrigerated Bakery | 1.2 | 20 | Off Cycle | 115 | 0.3 | 4.2 |  | 36 | 504 | 0
16S39V1/6B4V1 |  | 22' | S39V1 / B4V1 |  |  | Cold Deli / Dry Bakery | 6.32 | 20 | Off Cycle | 115 | 0.3 | 8.6 |  | 36 | 1032 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
8S1AG1 |  | 8' | S1AG1 |  |  | Self Serve Deli | 4.16 | 15 | HG 2 Wire | 115 | 0.8 | 0 | 1.1 | 96 | 0 | 132 | ME14S250 |  | SORIT 12 |  | 7/8 | 5/8 | 5/8
12S1AG1 |  | 12' | S1AG1 |  |  | Self Serve Deli | 6.24 | 15 | HG 2 Wire | 115 | 1.7 | 0 | 1.7 | 204 | 0 | 204 | ME14S250 |  | SORIT 12 |  | 7/8 | 5/8 | 5/8
8'8S1AG1 |  | 8'8' | 16' S1AG1 |  |  | Self Serve Deli | 8.32 | 15 | HG 2 Wire | 115 | 1.8 |  | 2.2 | 216 | 0 | 264 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
8'12S1AG1 |  | 8'12' | 20' S1AG1 |  |  | Self Serve Deli | 10.4 | 15 | HG 2 Wire | 115 | 2.5 |  | 2.8 | 300 | 0 | 336 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
12'12S1AG1 |  | 12'12' | 24' S1AG1 |  |  | Self Serve Deli | 12.48 | 15 | HG 2 Wire | 115 | 3.4 |  | 3.4 | 408 | 0 | 408 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6S1AG1 |  | 6' | S1AG1 |  |  | Self Serve Deli | 3.2 | 15 | HG 2 Wire | 115 | 0.8 |  | 1.1 | 96 | 0 | 132 | ME14S250 |  | SORIT 12 |  |  | 3/8 | 1/2
8'8S1AG1/1 |  | 8'8' | 16' S1AG1 |  |  | Self Serve Deli | 12.88 | 15 | HG 2 Wire | 115 | 1.9 |  | 2.1 | 228 | 0 | 252 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
[14 empty] | 0 | 0 | 0
4D6S1 |  | 4' | D6S1 |  |  | Dairy / Deli | 8.5 | 15 | Off Cycle | 115 | 0.5 | 0.8 |  | 60 | 96 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
6D6S1 |  | 6' | D6S1 |  |  | Dairy / Deli | 9.75 | 15 | Off Cycle | 115 | 1 | 1.2 |  | 120 | 144 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
8D6S1 |  | 8' | D6S1 |  |  | Dairy / Deli | 17 | 15 | Off Cycle | 115 | 1 | 1.6 |  | 120 | 192 | 0 |  |  | SORIT 12 |  |  | 7/8
8IL1 |  | 8' | IL1 | 1 |  | Meat Promo | 3.2 | -20 | HG 2 Wire | 115 | 1.26 |  | 1.39 | 151.2 | 0 | 166.8 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
8'8IL1 |  | 8'8' | IL1 | 1 |  | Meat Promo | 6.4 | -20 | HG 2 Wire | 115 | 2.52 |  | 2.78 | 302.4 | 0 | 333.6 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
12IL1 |  | 12' | IL1 | 1 |  | Meat Promo | 4.8 | -20 | HG 2 Wire | 115 | 1.6 |  | 2.43 | 192 | 0 | 291.6 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
8M3AG1 |  | 8' | M3AG1 |  |  | Self Serve Deli | 8 | 15 | RF 4 Wire | 115 | 0.8 | 0.9 | 1 | 96 | 108 | 120 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
12M3AG1 |  | 12' | M3AG1 |  |  | Self Serve Deli | 12 | 15 | RF 4 Wire | 115 | 1.2 | 1.4 | 1.5 | 144 | 168 | 180 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
8'8M3AG1 |  | 8'8' | 16' M3AG1 |  |  | Self Serve Deli | 16 | 15 | RF 4 Wire | 115 | 1.56 | 1.84 | 2.06 | 187.2 | 220.8 | 247.2 |  |  | SORIT 12 |  |  | 7/8 | 1/2
8M3AG1/1 |  | 8' | M3AG1/1 |  |  | Self Serve Deli | 12 | 15 | RF 4 Wire | 115 | 0.8 | 0.9 | 1 | 96 | 108 | 120 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
8M3AG1/2 |  | 8' | M3AG1/2 |  |  | Self Serve Deli | 16 | 15 | RF 4 Wire | 115 | 0.8 | 0.9 | 1 | 96 | 108 | 120 |  |  | SORIT 12 |  |  | 7/8 | 1/2
6'6M3AG1/1 |  | 6'6' | M3AG1/1 |  |  | Self Serve Deli | 16 | 15 | RF 4 Wire | 115 | 0.8 | 1.6 | 1.8 | 96 | 192 | 216
8'12M3AG1/1 |  | 8'12' | 20' M3AG1/1 |  |  | Self Serve Deli | 24 | 15 | RF 4 Wire | 115 | 2 | 2.3 | 2.5 | 240 | 276 | 300
8'8M3AG1/1 |  | 8'8' | 16' M3AG1/1 |  |  | Self Serve Deli | 20 | 15 | RF 4 Wire | 115 | 1.6 | 1.8 | 2.1 | 192 | 216 | 252 |  |  | SORIT 12 |  |  | 7/8
|  |  | WEDGE |  |  |  | 4 | 15
6B3A1 |  | 6' | B3A1 |  |  | Refrigerated Bakery | 6 | 15 | Off Cycle | 115 | 1.1 | 3.5 | 0 | 132 | 420 | 0 |  |  | SORIT 12 |  |  | 1/2 | 1/2
8B3A1 |  | 8' | B3A1 |  |  | Refrigerated Bakery | 8 | 15 | Off Cycle | 115 | 1.6 | 3.5 | 0 | 192 | 420 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
12B3A1 |  | 12' | B3A1 |  |  | Refrigerated Bakery | 12 | 15 | Off Cycle | 115 | 2.4 | 5.2 | 0 | 288 | 624 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
8'8B3A1 |  | 8'8' | 16' B3A1 |  |  | Refrigerated Bakery | 16 | 15 | Off Cycle | 115 | 3.2 | 7 | 0 | 384 | 840 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
8B3A1/1 |  | 8' | B3A1/1 |  |  | Refrigerated Bakery | 16 | 15 | Off Cycle | 115 | 1.6 | 3.5 | 0 | 192 | 420 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
8B3A1/2 |  | 8' | B3A1/2 |  |  | Refrigerated Bakery | 16 | 15 | Off Cycle | 115 | 1.6 | 3.5 | 0 | 192 | 420 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'8B3A1/1 |  | 8'8' | 16' B3A1/1 |  |  | Refrigerated Bakery | 20 | 15 | Off Cycle | 115 | 3.2 | 7 | 0 | 384 | 840 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
6'8B3A1 |  | 6'8' | 14' B3A1 |  |  | Refrigerated Bakery | 14 | 15 | Off Cycle | 115 | 2.7 | 7 | 0 | 324 | 840 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
|  |  | WEDGE |  |  |  | 4 | 15
8C1WI |  | 8' | C1WI |  |  | Cheese | 7.3 | 15 | Off Cycle | 115 | 1 |  | 0.4 | 120 | 0 | 48 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
12C1WI |  | 12' | C1WI |  |  | Cheese | 10.88 | 15 | Off Cycle | 115 | 1.5 |  | 0.7 | 180 | 0 | 84 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
7X10 |  | 7'X10'X8.5' | YAA1-66 |  | EGVE 3/4C | Deli Cooler | 5.9 | 20 | Off Cycle | 115 | 2 |  |  | 240 | 0 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
PREP |  |  |  |  | EGVE |  |  | 30 | Off Cycle | 115 |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
PCOOLER |  |  |  |  | EGVE | Produce Cooler |  | 25 | Off Cycle | 115 |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
DCOOLER |  |  |  |  | EGVE | Dairy Cooler |  | 20 | Off Cycle | 115 |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
MCOOLER |  |  |  |  | EGVE |  |  | 20 | HG 2 Wire | 230/1 | [6 empty] | ME14S250
MFREEZER |  |  |  | 1 | EGVE 3/4ZP | Meat Freezer |  | -15 | HG 2 Wire | 230/1 | [6 empty] | ME14S250 | ME14S250 | ME19S270 |  |  | 7/8 | 5/8
SFREEZER |  |  |  | 1 | EGVE1 1/2ZP | Storage Freezer |  | -15 | HG 2 Wire | 230/1 | [6 empty] | ME14S250 | ME14S250 | ME34S2110 |  | 1 3/8 | 1 3/8 | 5/8
10X15 |  | 10'X15'X8.5' | SAG3-140 | 1 | EGVE1 1/2ZP | Bakery Freezer | 12.45 | -15 | HG 2 Wire | 230/1 | 3 | [5 empty] | ME14S250 | ME14S250 | ME19S270 |  | 1 3/8 | 1 1/8 | 5/8
12X15 |  | 12'X15'X8.5 | XAG5-180 | 1 | EGVE1 1/2ZP | Ice Cream Freezer | 13.65 | -25 | HG 2 Wire | 230/1 | 5 | [5 empty] | ME14S250 | ME14S250 | ME25S290 |  | 1 3/8 | 1 1/8 | 5/8
5RSS |  | 5' | RSS |  |  | Self Serve Bakery | 6.718 | 20 | Off Cycle | 115 | 1.2 | 0.8 |  | 144 | 96 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
6RSS |  | 6' | RSS |  |  | Self Serve Bakery | 7.28 | 20 | Off Cycle | 115 | 1.2 | 1 |  | 144 | 120 | 0 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
5'5'6RSS |  | 5'5'6' | 16' RSS |  |  | Self Serve Bakery | 20.716 | 20 | Off Cycle | 115 | 3.6 | 2.6 |  | 432 | 312 | 0 |  |  | SORIT 12 |  |  | 7/8
5'5RSS |  | 5'5' | 10' RSS |  |  | Self Serve Bakery | 13.436 | 20 | Off Cycle | 115 | 2.4 | 1.6 |  | 288 | 192 | 0 |  |  | SORIT 12
5'6'RSS |  | 5'6' | 11' RSS |  |  | Self Serve Bakery | 13.998 | 20 | Off Cycle | 115 | 2.4 | 1.8 |  | 288 | 216 | 0 |  |  | SORIT 12
6'6RSS |  | 6'6' | 12' RSS |  |  | Self Serve Bakery | 14.56 | 20 | Off Cycle | 115 | 2.4 | 2 |  | 288 | 240 | 0 |  |  | SORIT 12
|  | HZVS1 PRODUCE | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8HZVS1 |  | 8' | HZVS1 |  |  | Produce | 6.05 | 20 | Off Cycle | 115 | 1 | 2.1 |  | 120 | 252 | 0 |  |  | SORIT 12 |  |  | 1/2
12HZVS1 |  | 12' | HZVS1 |  |  | Produce | 9.075 | 20 | Off Cycle | 115 | 1.5 | 4.2 |  | 180 | 504 | 0 |  |  | SORIT 12 |  |  | 5/8
8'8HZVS1 |  | 8'8' | 16' HZVS1 |  |  | Produce | 12.1 | 20 | Off Cycle | 115 | 2 | 4.2 |  | 240 | 504 | 0 |  |  | SORIT 12 |  |  | 5/8
8'12HZVS1 |  | 8'12' | 20' HZVS1 |  |  | Produce | 15.125 | 20 | Off Cycle | 115 | 2.5 | 6.3 |  | 300 | 756 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'8HZVS1 |  | 8'8'8' | 24' HZVS1 |  |  | Produce | 18.15 | 20 | Off Cycle | 115 | 3 | 6.3 |  | 360 | 756 | 0 |  |  | SORIT 12 |  |  | 7/8
12'12HZVS1 |  | 12'12' | 24' HZVS1 |  |  | Produce | 18.15 | 20 | Off Cycle | 115 | 3 | 8.4 |  | 360 | 1008 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'12HZVS1 |  | 8'8'12' | 28' HZVS1 |  |  | Produce | 21.175 | 20 | Off Cycle | 115 | 3.5 | 8.4 |  | 420 | 1008 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'8'8HZVS1 |  | 8'8'8'8' | 32' HZVS1 |  |  | Produce | 24.2 | 20 | Off Cycle | 115 | 4 | 8.4 |  | 480 | 1008 | 0 |  |  | SORIT 12 |  |  | 1 1/8
8'12'12HZVS1 |  | 8'12'12' | 32' HZVS1 |  |  | Produce | 24.2 | 20 | Off Cycle | 115 | 4 | 10.5 |  | 480 | 1260 | 0 |  |  | SORIT 12 |  |  | 1 1/8
8'8'8'12HZVS1 |  | 8'8'8'12' | 36' HZVS1 |  |  | Produce | 27.225 | 20 | Off Cycle | 115 | 4.5 | 10.5 |  | 540 | 1260 | 0 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
12'12'12HZVS1 |  | 12'12'12' | 36' HZVS1 |  |  | Produce | 27.225 | 20 | Off Cycle | 115 | 4.5 | 12.6 |  | 540 | 1512 | 0 |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8'8'8HZVS1 |  | 8'8'8'8'8' | 40' HZVS1 |  |  | Produce | 30.25 | 20 | Off Cycle | 115 | 5 | 10.5 |  | 600 | 1260 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12HZVS1 |  | 8'8'12'12' | 40' HZVS1 |  |  | Produce | 30.25 | 20 | Off Cycle | 115 | 5 | 12.6 |  | 600 | 1512 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'12HZVS1 |  | 8'8'8'8'12' | 44' HZVS1 |  |  | Produce | 33.275 | 20 | Off Cycle | 115 | 5.5 | 12.6 |  | 660 | 1512 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'12'12'12HZVS1 |  | 8'12'12'12' | 44' HZVS1 |  |  | Produce | 33.275 | 20 | Off Cycle | 115 | 5.5 | 14.7 |  | 660 | 1764 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'12'12HZVS1 |  | 8'8'8'12'12' | 48' HZVS1 |  |  | Produce | 36.3 | 20 | Off Cycle | 115 | 6 | 14.7 |  | 720 | 1764 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12'12HZVS1 |  | 12'12'12'12' | 48' HZVS1 |  |  | Produce | 36.3 | 20 | Off Cycle | 115 | 6 | 16.8 |  | 720 | 2016 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | M4AL1 MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8M4AL1 |  | 8' | M4AL1 | 1 |  | MD Fresh Meat | 11.2 | 12 | HG 2 Wire | 115 | 0.7 | 4.7 | 0.5 | 84 | 564 | 60 | ME14S250 |  | SORIT 12 |  |  | 7/8
12M4AL1 |  | 12' | M4AL1 | 1 |  | MD Fresh Meat | 16.8 | 12 | HG 2 Wire | 115 | 1 | 7 | 0.8 | 120 | 840 | 96 | ME14S250 |  | SORIT 12 |  |  | 7/8
8'8M4AL1 |  | 8'8' | 16' M4AL1 | 1 |  | MD Fresh Meat | 22.4 | 12 | HG 2 Wire | 115 | 1.4 | 9.4 | 1 | 168 | 1128 | 120 | ME14S250 |  | SORIT 12 |  |  | 1 1/8
8'12M4AL1 |  | 8'12' | 20' M4AL1 | 1 |  | MD Fresh Meat | 28 | 12 | HG 2 Wire | 115 | 1.7 | 11.7 | 1.3 | 204 | 1404 | 156 | ME14S250 |  | SORIT 15 |  |  | 1 1/8
8'8'8M4AL1 |  | 8'8'8' | 24' M4AL1 | 1 |  | MD Fresh Meat | 33.6 | 12 | HG 2 Wire | 115 | 2.1 | 14.1 | 1.5 | 252 | 1692 | 180 | ME14S250 |  | SORIT 15 |  |  | 1 3/8
12'12M4AL1 |  | 12'12' | 24' M4AL1 | 1 |  | MD Fresh Meat | 33.6 | 12 | HG 2 Wire | 115 | 2 | 14 | 1.6 | 240 | 1680 | 192 | ME14S250 |  | SORIT 15 |  |  | 1 3/8
8'8'12M4AL1 |  | 8'8'12' | 28' M4AL1 | 1 |  | MD Fresh Meat | 39.2 | 12 | HG 2 Wire | 115 | 2.4 | 16.4 | 1.8 | 288 | 1968 | 216 | ME14S250 |  | SORIT 20 |  |  | 1 3/8
8'8'8'8M4AL1 |  | 8'8'8'8' | 32' M4AL1 | 1 |  | MD Fresh Meat | 44.8 | 12 | HG 2 Wire | 115 | 2.8 | 18.8 | 2 | 336 | 2256 | 240 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
8'12'12M4AL1 |  | 8'12'12' | 32' M4AL1 | 1 |  | MD Fresh Meat | 44.8 | 12 | HG 2 Wire | 115 | 2.7 | 18.7 | 2.1 | 324 | 2244 | 252 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
8'8'8'12M4AL1 |  | 8'8'8'12' | 36' M4AL1 | 1 |  | MD Fresh Meat | 50.4 | 12 | HG 2 Wire | 115 | 3.1 | 21.1 | 2.3 | 372 | 2532 | 276 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
12'12'12M4AL1 |  | 12'12'12' | 36' M4AL1 | 1 |  | MD Fresh Meat | 50.4 | 12 | HG 2 Wire | 115 | 3 | 21 | 2.4 | 360 | 2520 | 288 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'8M4AL1 |  | 8'8'8'8'8' | 40' M4AL1 | 1 |  | MD Fresh Meat | 56 | 12 | HG 2 Wire | 115 | 3.5 | 23.5 | 2.5 | 420 | 2820 | 300 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
8'8'12'12M4AL1 |  | 8'8'12'12' | 40' M4AL1 | 1 |  | MD Fresh Meat | 56 | 12 | HG 2 Wire | 115 | 3.4 | 23.4 | 2.6 | 408 | 2808 | 312 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'12M4AL1 |  | 8'8'8'8'12' | 44' M4AL1 | 1 |  | MD Fresh Meat | 61.6 | 12 | HG 2 Wire | 115 | 3.8 | 25.8 | 2.8 | 456 | 3096 | 336 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
8'12'12'12M4AL1 |  | 8'12'12'12' | 44' M4AL1 | 1 |  | MD Fresh Meat | 61.6 | 12 | HG 2 Wire | 115 | 3.7 | 25.7 | 2.9 | 444 | 3084 | 348 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
8'8'8'12'12M4AL1 |  | 8'8'8'12'12' | 48' M4AL1 | 1 |  | MD Fresh Meat | 67.2 | 12 | HG 2 Wire | 115 | 4.1 | 28.1 | 3.1 | 492 | 3372 | 372 | ME14S250 |  | SORIT 20 |  |  | 2 1/8
12'12'12'12M4AL1 |  | 12'12'12'12' | 48' M4AL1 | 1 |  | MD Fresh Meat | 67.2 | 12 | HG 2 Wire | 115 | 4 | 28 | 3.2 | 480 | 3360 | 384 | ME14S250 |  | SORIT 20 |  |  | 2 1/8
FOR USE WITH +10 SUCTION AND +115/+110 CONDENSING TEMPS
|  | M1A1 FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8M1A1 |  | 8' | M1A1 | 1 |  | Fresh Meat | 4.16 | 15 | HG 2 Wire | 115 | 0.3 |  | 0.7 | 36 | 0 | 84 | ME14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
12M1A1 |  | 12' | M1A1 | 1 |  | Fresh Meat | 6.24 | 15 | HG 2 Wire | 115 | 0.7 |  | 1.2 | 84 | 0 | 144 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
8'8M1A1 |  | 8'8' | 16' M1A1 | 1 |  | Fresh Meat | 8.32 | 15 | HG 2 Wire | 115 | 0.6 | 0 | 1.4 | 72 | 0 | 168 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
8'12M1A1 |  | 8'12' | 20'M1A1 | 1 |  | Fresh Meat | 10.4 | 15 | HG 2 Wire | 115 | 1 | 0 | 1.9 | 120 | 0 | 228 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8M1A1 |  | 8'8'8' | 24' M1A1 | 1 |  | Fresh Meat | 12.48 | 15 | HG 2 Wire | 115 | 0.9 | 0 | 2.1 | 108 | 0 | 252 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
12'12M1A1 |  | 12'12' | 24' M1A1 | 1 |  | Fresh Meat | 12.48 | 15 | HG 2 Wire | 115 | 1.4 | 0 | 2.4 | 168 | 0 | 288 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'12M1A1 |  | 8'8'12' | 28' M1A1 | 1 |  | Fresh Meat | 14.56 | 15 | HG 2 Wire | 115 | 1.3 | 0 | 2.6 | 156 | 0 | 312 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'8M1A1 |  | 8'8'8'8' | 32' M1A1 | 1 |  | Fresh Meat | 16.64 | 15 | HG 2 Wire | 115 | 1.2 | 0 | 2.8 | 144 | 0 | 336 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'12'12M1A1 |  | 8'12'12' | 32' M1A1 | 1 |  | Fresh Meat | 16.64 | 15 | HG 2 Wire | 115 | 1.7 | 0 | 3.1 | 204 | 0 | 372 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'12M1A1 |  | 8'8'8'12' | 36' M1A1 | 1 |  | Fresh Meat | 18.72 | 15 | HG 2 Wire | 115 | 1.6 | 0 | 3.3 | 192 | 0 | 396 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
12'12'12M1A1 |  | 12'12'12' | 36' M1A1 | 1 |  | Fresh Meat | 18.72 | 15 | HG 2 Wire | 115 | 2.1 | 0 | 3.6 | 252 | 0 | 432 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8'8'8'8M1A1 |  | 8'8'8'8'8' | 40' M1A1 | 1 |  | Fresh Meat | 20.8 | 15 | HG 2 Wire | 115 | 1.5 | 0 | 3.5 | 180 | 0 | 420 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'12'12M1A1 |  | 8'8'12'12' | 40' M1A1 | 1 |  | Fresh Meat | 20.8 | 15 | HG 2 Wire | 115 | 2 | 0 | 3.8 | 240 | 0 | 456 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8'8'12M1A1 |  | 8'8'8'8'12' | 44' M1A1 | 1 |  | Fresh Meat | 22.88 | 15 | HG 2 Wire | 115 | 1.9 | 0 | 4 | 228 | 0 | 480 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'12'12'12M1A1 |  | 8'12'12'12' | 44' M1A1 | 1 |  | Fresh Meat | 22.88 | 15 | HG 2 Wire | 115 | 2.4 | 0 | 4.3 | 288 | 0 | 516 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'8'8'12'12M1A1 |  | 8'8'8'12'12' | 48' M1A1 | 1 |  | Fresh Meat | 24.96 | 15 | HG 2 Wire | 115 | 2.3 | 0 | 4.5 | 276 | 0 | 540 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12'12M1A1 |  | 12'12'12'12' | 48' M1A1 | 1 |  | Fresh Meat | 24.96 | 15 | HG 2 Wire | 115 | 2.8 | 0 | 4.8 | 336 | 0 | 576 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'12'12'12M1A1 |  | 8'8'12'12'12' | 52' M1A1 | 1 |  | Fresh Meat | 27.04 | 15 | HG 2 Wire | 115 | 2.7 | 0 | 5 | 324 | 0 | 600 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
52 |  |  | 52' M1A1 | 1 |  | Fresh Meat |  | 15 | HG 2 Wire | 115 |  |  |  | 0 | 0 | 0 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'12'12'12'12M1A1 |  | 8'12'12'12'12 | 56' M1A1 | 1 |  | Fresh Meat | 29.12 | 15 | HG 2 Wire | 115 | 3.1 | 0 | 5.5 | 372 | 0 | 660 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
56 |  |  | M1A1 | 1 |  | Fresh Meat | 30.52 | 15 | HG 2 Wire | 115 |  |  |  | 0 | 0 | 0 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | LV5H1 WITH EPR | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2LV5H1S |  | 2 | LV5H1 | 1 |  | Frozen Food | 3 | -15 | HG 2 Wire | 115 | 0.9 | 2.2 | 3.4 | 108 | 264 | 408 | ME14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
3LV5H1S |  | 3 | LV5H1 | 1 |  | Frozen Food | 4.5 | -15 | HG 2 Wire | 115 | 1.4 | 2.2 | 4.8 | 168 | 264 | 576 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4LV5H1S |  | 4 | LV5H1 | 1 |  | Frozen Food | 6 | -15 | HG 2 Wire | 115 | 2 | 6.3 | 6.2 | 240 | 756 | 744 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5LV5H1S |  | 5 | LV5H1 | 1 |  | Frozen Food | 7.5 | -15 | HG 2 Wire | 115 | 2.5 | 6.3 | 7.7 | 300 | 756 | 924 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3LV5H1S |  | 3,3 | 6Dr LV5H1 | 1 |  | Frozen Food | 9 | -15 | HG 2 Wire | 115 | 2.8 | 4.4 | 9.6 | 336 | 528 | 1152 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3LV5H1S |  | 4,3 | 7Dr LV5H1 | 1 |  | Frozen Food | 10.5 | -15 | HG 2 Wire | 115 | 3.4 | 8.5 | 11 | 408 | 1020 | 1320 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4LV5H1S |  | 4,4 | 8Dr LV5H1 | 1 |  | Frozen Food | 12 | -15 | HG 2 Wire | 115 | 4 | 12.6 | 12.4 | 480 | 1512 | 1488 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3LV5H1S |  | 5,3 | 8Dr LV5H1 | 1 |  | Frozen Food | 12 | -15 | HG 2 Wire | 115 | 3.9 | 8.5 | 12.5 | 468 | 1020 | 1500 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4LV5H1S |  | 5,4 | 9Dr LV5H1 | 1 |  | Frozen Food | 13.5 | -15 | HG 2 Wire | 115 | 4.5 | 12.6 | 13.9 | 540 | 1512 | 1668 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3LV5H1S |  | 3,3,3 | 9Dr LV5H1 | 1 |  | Frozen Food | 13.5 | -15 | HG 2 Wire | 115 | 4.2 | 6.6 | 14.4 | 504 | 792 | 1728 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5LV5H1S |  | 5,5 | 10Dr LV5H1 | 1 |  | Frozen Food | 15 | -15 | HG 2 Wire | 115 | 5 | 12.6 | 15.4 | 600 | 1512 | 1848 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3LV5H1S |  | 4,3,3 | 10Dr LV5H1 | 1 |  | Frozen Food | 15 | -15 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.8 | 576 | 1284 | 1896 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3LV5H1S |  | 5,3,3 | 11Dr LV5H1 | 1 |  | Frozen Food | 16.5 | -15 | HG 2 Wire | 115 | 5.3 | 10.7 | 17.3 | 636 | 1284 | 2076 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3LV5H1S |  | 4,4,3 | 11Dr LV5H1 | 1 |  | Frozen Food | 16.5 | -15 | HG 2 Wire | 115 | 5.4 | 14.8 | 17.2 | 648 | 1776 | 2064 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4LV5H1S |  | 4,4,4 | 12Dr LV5H1 | 1 |  | Frozen Food | 18 | -15 | HG 2 Wire | 115 | 6 | 18.9 | 18.6 | 720 | 2268 | 2232 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3LV5H1S |  | 5,4,3 | 12Dr LV5H1 | 1 |  | Frozen Food | 18 | -15 | HG 2 Wire | 115 | 5.9 | 14.8 | 18.7 | 708 | 1776 | 2244 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4LV5H1S |  | 5,4,4 | 13Dr LV5H1 | 1 |  | Frozen Food | 19.5 | -15 | HG 2 Wire | 115 | 6.5 | 18.9 | 20.1 | 780 | 2268 | 2412 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3LV5H1S |  | 5,5,3 | 13Dr LV5H1 | 1 |  | Frozen Food | 19.5 | -15 | HG 2 Wire | 115 | 6.4 | 14.8 | 20.2 | 768 | 1776 | 2424 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4LV5H1S |  | 5,5,4 | 14Dr LV5H1 | 1 |  | Frozen Food | 21 | -15 | HG 2 Wire | 115 | 7 | 18.9 | 21.6 | 840 | 2268 | 2592 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3LV5H1S |  | 4,4,3,3 | 14Dr LV5H1 | 1 |  | Frozen Food | 21 | -15 | HG 2 Wire | 115 | 6.8 | 17 | 22 | 816 | 2040 | 2640 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5LV5H1S |  | 5,5,5 | 15Dr LV5H1 | 1 |  | Frozen Food | 22.5 | -15 | HG 2 Wire | 115 | 7.5 | 18.9 | 23.1 | 900 | 2268 | 2772 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3LV5H1S |  | 4,4,4,3 | 15Dr LV5H1 | 1 |  | Frozen Food | 22.5 | -15 | HG 2 Wire | 115 | 7.4 | 21.1 | 23.4 | 888 | 2532 | 2808 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3LV5H1S |  | 5,5,3,3 | 16Dr LV5H1 | 1 |  | Frozen Food | 24 | -15 | HG 2 Wire | 115 | 7.8 | 17 | 25 | 936 | 2040 | 3000 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4LV5H1S |  | 4,4,4,4 | 16Dr LV5H1 | 1 |  | Frozen Food | 24 | -15 | HG 2 Wire | 115 | 8 | 25.2 | 24.8 | 960 | 3024 | 2976 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,3,2LV5H1S | * | 4,3,2 | 9Dr LV5H1 | 1 |  | Frozen Food | 14.5 | -15 | HG 2 Wire | 115 | 4.3 | 10.7 | 14.4 | 516 | 1284 | 1728 | ME14S250 |  | SORIT 20 |  |  | 1 1/8 | 5/8
5,3,2LV5H1S | * | 5,3,2 | 10Dr LV5H1 | 1 |  | Frozen Food | 15 | -15 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.9 | 576 | 1284 | 1908 | ME14S250 |  | SORIT 20 |  |  | 1 1/8 | 5/8
5,3,3,3LV5H1S |  | 5,3,3,3 | 14Dr LV5H1 | 1 |  | Frozen Food | 21 | -15 | HG 2 Wire | 115 | 6.7 | 12.9 | 22.1 | 804 | 1548 | 2652 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2LV5H1S |  | 4,4,3,2 | 13Dr LV5H1 | 1 |  | Frozen Food | 19.5 | -15 | HG 2 Wire | 115 | 6.3 | 17 | 20.6 | 756 | 2040 | 2472 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | LV5H1 WITH SUCTION STOP | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2LV5H1SS |  | 2 | LV5H1 | 1 |  | Frozen Food | 3 | -15 | HG 2 Wire | 115 | 0.9 | 2.2 | 3.4 | 108 | 264 | 408 | ME14S250 |  | ME14S250 |  |  | 1/2 | 1/2
3LV5H1SS |  | 3 | LV5H1 | 1 |  | Frozen Food | 4.5 | -15 | HG 2 Wire | 115 | 1.4 | 2.2 | 4.8 | 168 | 264 | 576 | ME14S250 |  | ME14S250 |  |  | 5/8 | 1/2
4LV5H1SS |  | 4 | LV5H1 | 1 |  | Frozen Food | 6 | -15 | HG 2 Wire | 115 | 2 | 6.3 | 6.2 | 240 | 756 | 744 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
5LV5H1SS |  | 5 | LV5H1 | 1 |  | Frozen Food | 7.5 | -15 | HG 2 Wire | 115 | 2.5 | 6.3 | 7.7 | 300 | 756 | 924 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
3,3LV5H1SS |  | 3,3 | 6Dr LV5H1 | 1 |  | Frozen Food | 9 | -15 | HG 2 Wire | 115 | 2.8 | 4.4 | 9.6 | 336 | 528 | 1152 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
4,3LV5H1SS |  | 4,3 | 7Dr LV5H1 | 1 |  | Frozen Food | 10.5 | -15 | HG 2 Wire | 115 | 3.4 | 8.5 | 11 | 408 | 1020 | 1320 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
4,4LV5H1SS |  | 4,4 | 8Dr LV5H1 | 1 |  | Frozen Food | 12 | -15 | HG 2 Wire | 115 | 4 | 12.6 | 12.4 | 480 | 1512 | 1488 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
5,3LV5H1SS |  | 5,3 | 8Dr LV5H1 | 1 |  | Frozen Food | 12 | -15 | HG 2 Wire | 115 | 3.9 | 8.5 | 12.5 | 468 | 1020 | 1500 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
5,4LV5H1SS |  | 5,4 | 9Dr LV5H1 | 1 |  | Frozen Food | 13.5 | -15 | HG 2 Wire | 115 | 4.5 | 12.6 | 13.9 | 540 | 1512 | 1668 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
3,3,3LV5H1SS |  | 3,3,3 | 9Dr LV5H1 | 1 |  | Frozen Food | 13.5 | -15 | HG 2 Wire | 115 | 4.2 | 6.6 | 14.4 | 504 | 792 | 1728 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,5LV5H1SS |  | 5,5 | 10Dr LV5H1 | 1 |  | Frozen Food | 15 | -15 | HG 2 Wire | 115 | 5 | 12.6 | 15.4 | 600 | 1512 | 1848 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,3,3LV5H1SS |  | 4,3,3 | 10Dr LV5H1 | 1 |  | Frozen Food | 15 | -15 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.8 | 576 | 1284 | 1896 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,3,3LV5H1SS |  | 5,3,3 | 11Dr LV5H1 | 1 |  | Frozen Food | 16.5 | -15 | HG 2 Wire | 115 | 5.3 | 10.7 | 17.3 | 636 | 1284 | 2076 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,4,3LV5H1SS |  | 4,4,3 | 11Dr LV5H1 | 1 |  | Frozen Food | 16.5 | -15 | HG 2 Wire | 115 | 5.4 | 14.8 | 17.2 | 648 | 1776 | 2064 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,4,4LV5H1SS |  | 4,4,4 | 12Dr LV5H1 | 1 |  | Frozen Food | 18 | -15 | HG 2 Wire | 115 | 6 | 18.9 | 18.6 | 720 | 2268 | 2232 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,4,3LV5H1SS |  | 5,4,3 | 12Dr LV5H1 | 1 |  | Frozen Food | 18 | -15 | HG 2 Wire | 115 | 5.9 | 14.8 | 18.7 | 708 | 1776 | 2244 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,4,4LV5H1SS |  | 5,4,4 | 13Dr LV5H1 | 1 |  | Frozen Food | 19.5 | -15 | HG 2 Wire | 115 | 6.5 | 18.9 | 20.1 | 780 | 2268 | 2412 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,3LV5H1SS |  | 5,5,3 | 13Dr LV5H1 | 1 |  | Frozen Food | 19.5 | -15 | HG 2 Wire | 115 | 6.4 | 14.8 | 20.2 | 768 | 1776 | 2424 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,4LV5H1SS |  | 5,5,4 | 14Dr LV5H1 | 1 |  | Frozen Food | 21 | -15 | HG 2 Wire | 115 | 7 | 18.9 | 21.6 | 840 | 2268 | 2592 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,3,3LV5H1SS |  | 4,4,3,3 | 14Dr LV5H1 | 1 |  | Frozen Food | 21 | -15 | HG 2 Wire | 115 | 6.8 | 17 | 22 | 816 | 2040 | 2640 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,5LV5H1SS |  | 5,5,5 | 15Dr LV5H1 | 1 |  | Frozen Food | 22.5 | -15 | HG 2 Wire | 115 | 7.5 | 18.9 | 23.1 | 900 | 2268 | 2772 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,4,3LV5H1SS |  | 4,4,4,3 | 15Dr LV5H1 | 1 |  | Frozen Food | 22.5 | -15 | HG 2 Wire | 115 | 7.4 | 21.1 | 23.4 | 888 | 2532 | 2808 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,3,3LV5H1SS |  | 5,5,3,3 | 16Dr LV5H1 | 1 |  | Frozen Food | 24 | -15 | HG 2 Wire | 115 | 7.8 | 17 | 25 | 936 | 2040 | 3000 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,4,4LV5H1SS |  | 4,4,4,4 | 16Dr LV5H1 | 1 |  | Frozen Food | 24 | -15 | HG 2 Wire | 115 | 8 | 25.2 | 24.8 | 960 | 3024 | 2976 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,3,2LV5H1SS | * | 4,3,2 | 9Dr LV5H1 | 1 |  | Frozen Food | 13.5 | -15 | HG 2 Wire | 115 | 4.3 | 10.7 | 14.4 | 516 | 1284 | 1728 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,3,2LV5H1SS | * | 5,3,2 | 10Dr LV5H1 | 1 |  | Frozen Food | 15 | -15 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.9 | 576 | 1284 | 1908 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,3,3,3LV5H1SS |  | 5,3,3,3 | 14Dr LV5H1 | 1 |  | Frozen Food | 21 | -15 | HG 2 Wire | 115 | 6.7 | 12.9 | 22.1 | 804 | 1548 | 2652 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
|  | LV5H1 WITH EPR RUNNING ON -25 SUCTION GROUP | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2LV5H1S-25 |  | 2 | LV5H1 | 1 |  | Frozen Food | 3.4 | -25 | HG 2 Wire | 115 | 0.9 | 2.2 | 3.4 | 108 | 264 | 408 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3LV5H1S-25 |  | 3 | LV5H1 | 1 |  | Frozen Food | 5.1 | -25 | HG 2 Wire | 115 | 1.4 | 2.2 | 4.8 | 168 | 264 | 576 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4LV5H1S-25 |  | 4 | LV5H1 | 1 |  | Frozen Food | 6.8 | -25 | HG 2 Wire | 115 | 2 | 6.3 | 6.2 | 240 | 756 | 744 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5LV5H1S-25 |  | 5 | LV5H1 | 1 |  | Frozen Food | 8.5 | -25 | HG 2 Wire | 115 | 2.5 | 6.3 | 7.7 | 300 | 756 | 924 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3LV5H1S-25 |  | 3,3 | 6Dr LV5H1 | 1 |  | Frozen Food | 10.2 | -25 | HG 2 Wire | 115 | 2.8 | 4.4 | 9.6 | 336 | 528 | 1152 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3LV5H1S-25 |  | 4,3 | 7Dr LV5H1 | 1 |  | Frozen Food | 11.9 | -25 | HG 2 Wire | 115 | 3.4 | 8.5 | 11 | 408 | 1020 | 1320 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4LV5H1S-25 |  | 4,4 | 8Dr LV5H1 | 1 |  | Frozen Food | 13.6 | -25 | HG 2 Wire | 115 | 4 | 12.6 | 12.4 | 480 | 1512 | 1488 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3LV5H1S-25 |  | 5,3 | 8Dr LV5H1 | 1 |  | Frozen Food | 13.6 | -25 | HG 2 Wire | 115 | 3.9 | 8.5 | 12.5 | 468 | 1020 | 1500 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4LV5H1S-25 |  | 5,4 | 9Dr LV5H1 | 1 |  | Frozen Food | 15.3 | -25 | HG 2 Wire | 115 | 4.5 | 12.6 | 13.9 | 540 | 1512 | 1668 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
3,3,3LV5H1S-25 |  | 3,3,3 | 9Dr LV5H1 | 1 |  | Frozen Food | 15.3 | -25 | HG 2 Wire | 115 | 4.2 | 6.6 | 14.4 | 504 | 792 | 1728 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5LV5H1S-25 |  | 5,5 | 10Dr LV5H1 | 1 |  | Frozen Food | 17 | -25 | HG 2 Wire | 115 | 5 | 12.6 | 15.4 | 600 | 1512 | 1848 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3LV5H1S-25 |  | 4,3,3 | 10Dr LV5H1 | 1 |  | Frozen Food | 17 | -25 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.8 | 576 | 1284 | 1896 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3LV5H1S-25 |  | 5,3,3 | 11Dr LV5H1 | 1 |  | Frozen Food | 18.7 | -25 | HG 2 Wire | 115 | 5.3 | 10.7 | 17.3 | 636 | 1284 | 2076 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3LV5H1S-25 |  | 4,4,3 | 11Dr LV5H1 | 1 |  | Frozen Food | 18.7 | -25 | HG 2 Wire | 115 | 5.4 | 14.8 | 17.2 | 648 | 1776 | 2064 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4LV5H1S-25 |  | 4,4,4 | 12Dr LV5H1 | 1 |  | Frozen Food | 20.4 | -25 | HG 2 Wire | 115 | 6 | 18.9 | 18.6 | 720 | 2268 | 2232 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,4,3LV5H1S-25 |  | 5,4,3 | 12Dr LV5H1 | 1 |  | Frozen Food | 20.4 | -25 | HG 2 Wire | 115 | 5.9 | 14.8 | 18.7 | 708 | 1776 | 2244 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,4,4LV5H1S-25 |  | 5,4,4 | 13Dr LV5H1 | 1 |  | Frozen Food | 22.1 | -25 | HG 2 Wire | 115 | 6.5 | 18.9 | 20.1 | 780 | 2268 | 2412 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,3LV5H1S-25 |  | 5,5,3 | 13Dr LV5H1 | 1 |  | Frozen Food | 22.1 | -25 | HG 2 Wire | 115 | 6.4 | 14.8 | 20.2 | 768 | 1776 | 2424 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,4LV5H1S-25 |  | 5,5,4 | 14Dr LV5H1 | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 7 | 18.9 | 21.6 | 840 | 2268 | 2592 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,3LV5H1S-25 |  | 4,4,3,3 | 14Dr LV5H1 | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 6.8 | 17 | 22 | 816 | 2040 | 2640 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,5LV5H1S-25 |  | 5,5,5 | 15Dr LV5H1 | 1 |  | Frozen Food | 25.5 | -25 | HG 2 Wire | 115 | 7.5 | 18.9 | 23.1 | 900 | 2268 | 2772 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3LV5H1S-25 |  | 4,4,4,3 | 15Dr LV5H1 | 1 |  | Frozen Food | 25.5 | -25 | HG 2 Wire | 115 | 7.4 | 21.1 | 23.4 | 888 | 2532 | 2808 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3LV5H1S-25 |  | 5,5,3,3 | 16Dr LV5H1 | 1 |  | Frozen Food | 27.2 | -25 | HG 2 Wire | 115 | 7.8 | 17 | 25 | 936 | 2040 | 3000 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4LV5H1S-25 |  | 4,4,4,4 | 16Dr LV5H1 | 1 |  | Frozen Food | 27.2 | -25 | HG 2 Wire | 115 | 8 | 25.2 | 24.8 | 960 | 3024 | 2976 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,3,2LV5H1S-25 |  | 4,3,2 | 9Dr LV5H1 | 1 |  | Frozen Food | 13.5 | -25 | HG 2 Wire | 115 | 4.3 | 10.7 | 14.4 | 516 | 1284 | 1728 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3,2LV5H1S-25 |  | 5,3,2 | 10Dr LV5H1 | 1 |  | Frozen Food | 15 | -25 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.9 | 576 | 1284 | 1908 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3,3LV5H1S-25 |  | 5,3,3,3 | 14Dr LV5H1 | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 6.7 | 12.9 | 22.1 | 804 | 1548 | 2652 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | IV5H1 WITH SUCTION STOP | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2IV5H1 |  | 2 | IV5H1 | 1 |  | Ice Cream | 3.4 | -25 | HG 2 Wire | 115 | 0.9 | 2.2 | 3.4 | 108 | 264 | 408 | ME14S250 |  | ME14S250 |  |  | 5/8 | 1/2
3IV5H1 |  | 3 | IV5H1 | 1 |  | Ice Cream | 5.1 | -25 | HG 2 Wire | 115 | 1.4 | 2.2 | 4.8 | 168 | 264 | 576 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
4IV5H1 |  | 4 | IV5H1 | 1 |  | Ice Cream | 6.8 | -25 | HG 2 Wire | 115 | 2 | 6.3 | 6.2 | 240 | 756 | 744 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
5IV5H1 |  | 5 | IV5H1 | 1 |  | Ice Cream | 8.5 | -25 | HG 2 Wire | 115 | 2.5 | 6.3 | 7.7 | 300 | 756 | 924 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
3,3IV5H1 |  | 3,3 | 6Dr IV5H1 | 1 |  | Ice Cream | 10.2 | -25 | HG 2 Wire | 115 | 2.8 | 4.4 | 9.6 | 336 | 528 | 1152 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
4,3IV5H1 |  | 4,3 | 7Dr IV5H1 | 1 |  | Ice Cream | 11.9 | -25 | HG 2 Wire | 115 | 3.4 | 8.5 | 11 | 408 | 1020 | 1320 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
4,4IV5H1 |  | 4,4 | 8Dr IV5H1 | 1 |  | Ice Cream | 13.6 | -25 | HG 2 Wire | 115 | 4 | 12.6 | 12.4 | 480 | 1512 | 1488 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,3IV5H1 |  | 5,3 | 8Dr IV5H1 | 1 |  | Ice Cream | 13.6 | -25 | HG 2 Wire | 115 | 3.9 | 8.5 | 12.5 | 468 | 1020 | 1500 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,4IV5H1 |  | 5,4 | 9Dr IV5H1 | 1 |  | Ice Cream | 15.3 | -25 | HG 2 Wire | 115 | 4.5 | 12.6 | 13.9 | 540 | 1512 | 1668 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
3,3,3IV5H1 |  | 3,3,3 | 9Dr IV5H1 | 1 |  | Ice Cream | 15.3 | -25 | HG 2 Wire | 115 | 4.2 | 6.6 | 14.4 | 504 | 792 | 1728 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
5,5IV5H1 |  | 5,5 | 10Dr IV5H1 | 1 |  | Ice Cream | 17 | -25 | HG 2 Wire | 115 | 5 | 12.6 | 15.4 | 600 | 1512 | 1848 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
4,3,3IV5H1 |  | 4,3,3 | 10Dr IV5H1 | 1 |  | Ice Cream | 17 | -25 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.8 | 576 | 1284 | 1896 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
5,3,3IV5H1 |  | 5,3,3 | 11Dr IV5H1 | 1 |  | Ice Cream | 18.7 | -25 | HG 2 Wire | 115 | 5.3 | 10.7 | 17.3 | 636 | 1284 | 2076 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
4,4,3IV5H1 |  | 4,4,3 | 11Dr IV5H1 | 1 |  | Ice Cream | 18.7 | -25 | HG 2 Wire | 115 | 5.4 | 14.8 | 17.2 | 648 | 1776 | 2064 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
4,4,4IV5H1 |  | 4,4,4 | 12Dr IV5H1 | 1 |  | Ice Cream | 20.4 | -25 | HG 2 Wire | 115 | 6 | 18.9 | 18.6 | 720 | 2268 | 2232 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,4,3IV5H1 |  | 5,4,3 | 12Dr IV5H1 | 1 |  | Ice Cream | 20.4 | -25 | HG 2 Wire | 115 | 5.9 | 14.8 | 18.7 | 708 | 1776 | 2244 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,4,4IV5H1 |  | 5,4,4 | 13Dr IV5H1 | 1 |  | Ice Cream | 22.1 | -25 | HG 2 Wire | 115 | 6.5 | 18.9 | 20.1 | 780 | 2268 | 2412 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,3IV5H1 |  | 5,5,3 | 13Dr IV5H1 | 1 |  | Ice Cream | 22.1 | -25 | HG 2 Wire | 115 | 6.4 | 14.8 | 20.2 | 768 | 1776 | 2424 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,4IV5H1 |  | 5,5,4 | 14Dr IV5H1 | 1 |  | Ice Cream | 23.8 | -25 | HG 2 Wire | 115 | 7 | 18.9 | 21.6 | 840 | 2268 | 2592 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
4,4,3,3IV5H1 |  | 4,4,3,3 | 14Dr IV5H1 | 1 |  | Ice Cream | 23.8 | -25 | HG 2 Wire | 115 | 6.8 | 17 | 22 | 816 | 2040 | 2640 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
5,5,5IV5H1 |  | 5,5,5 | 15Dr IV5H1 | 1 |  | Ice Cream | 25.5 | -25 | HG 2 Wire | 115 | 7.5 | 18.9 | 23.1 | 900 | 2268 | 2772 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
4,4,4,3IV5H1 |  | 4,4,4,3 | 15Dr IV5H1 | 1 |  | Ice Cream | 25.5 | -25 | HG 2 Wire | 115 | 7.4 | 21.1 | 23.4 | 888 | 2532 | 2808 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
5,5,3,3IV5H1 |  | 5,5,3,3 | 16Dr IV5H1 | 1 |  | Ice Cream | 27.2 | -25 | HG 2 Wire | 115 | 7.8 | 17 | 25 | 936 | 2040 | 3000 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
4,4,4,4IV5H1 |  | 4,4,4,4 | 16Dr IV5H1 | 1 |  | Ice Cream | 27.2 | -25 | HG 2 Wire | 115 | 8 | 25.2 | 24.8 | 960 | 3024 | 2976 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
4,4,3,2IV5H1 |  | 4,4,3,2 | 13Dr IV5H1 | 1 |  | Ice Cream | 22.1 | -25 | HG 2 Wire | 115 | 4.3 | 10.7 | 14.4 | 516 | 1284 | 1728 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
|  | LV5H WITH SUCTION STOP | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
3LV5H |  | 3 | LV5H | 1 |  | Frozen Food | 5.1 | -25 | HG 2 Wire | 115 | 2.5 | 4 | 6.2 | 300 | 480 | 744 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4LV5H |  | 4 | LV5H | 1 |  | Frozen Food | 6.8 | -25 | HG 2 Wire | 115 | 3.3 | 7.8 | 8 | 396 | 936 | 960 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5LV5H |  | 5 | LV5H | 1 |  | Frozen Food | 8.5 | -25 | HG 2 Wire | 115 | 4.1 | 7.8 | 9.9 | 492 | 936 | 1188 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3LV5H |  | 3,3 | 6Dr LV5H | 1 |  | Frozen Food | 10.2 | -25 | HG 2 Wire | 115 | 5 | 8 | 12.4 | 600 | 960 | 1488 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3LV5H |  | 4,3 | 7Dr LV5H | 1 |  | Frozen Food | 11.9 | -25 | HG 2 Wire | 115 | 5.8 | 11.8 | 14.2 | 696 | 1416 | 1704 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4LV5H |  | 4,4 | 8Dr LV5H | 1 |  | Frozen Food | 13.6 | -25 | HG 2 Wire | 115 | 6.6 | 15.6 | 16 | 792 | 1872 | 1920 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3LV5H |  | 5,3 | 8Dr LV5H | 1 |  | Frozen Food | 13.6 | -25 | HG 2 Wire | 115 | 6.6 | 11.8 | 16.1 | 792 | 1416 | 1932 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4LV5H |  | 5,4 | 9Dr LV5H | 1 |  | Frozen Food | 15.3 | -25 | HG 2 Wire | 115 | 7.4 | 15.6 | 17.9 | 888 | 1872 | 2148 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
3,3,3LV5H |  | 3,3,3 | 9Dr LV5H | 1 |  | Frozen Food | 15.3 | -25 | HG 2 Wire | 115 | 7.5 | 12 | 18.6 | 900 | 1440 | 2232 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5LV5H |  | 5,5 | 10Dr LV5H | 1 |  | Frozen Food | 17 | -25 | HG 2 Wire | 115 | 8.2 | 15.6 | 19.8 | 984 | 1872 | 2376 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3LV5H |  | 4,3,3 | 10Dr LV5H | 1 |  | Frozen Food | 17 | -25 | HG 2 Wire | 115 | 8.3 | 15.8 | 20.4 | 996 | 1896 | 2448 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3LV5H |  | 5,3,3 | 11Dr LV5H | 1 |  | Frozen Food | 18.7 | -25 | HG 2 Wire | 115 | 9.1 | 15.8 | 22.3 | 1092 | 1896 | 2676 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3LV5H |  | 4,4,3 | 11Dr LV5H | 1 |  | Frozen Food | 18.7 | -25 | HG 2 Wire | 115 | 9.1 | 19.6 | 22.2 | 1092 | 2352 | 2664 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4LV5H |  | 4,4,4 | 12Dr LV5H | 1 |  | Frozen Food | 20.4 | -25 | HG 2 Wire | 115 | 9.9 | 23.4 | 24 | 1188 | 2808 | 2880 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,4,3LV5H |  | 5,4,3 | 12Dr LV5H | 1 |  | Frozen Food | 20.4 | -25 | HG 2 Wire | 115 | 9.9 | 19.6 | 24.1 | 1188 | 2352 | 2892 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,4,4LV5H |  | 5,4,4 | 13Dr LV5H | 1 |  | Frozen Food | 22.1 | -25 | HG 2 Wire | 115 | 10.7 | 23.4 | 25.9 | 1284 | 2808 | 3108 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,3LV5H |  | 5,5,3 | 13Dr LV5H | 1 |  | Frozen Food | 22.1 | -25 | HG 2 Wire | 115 | 10.7 | 19.6 | 26 | 1284 | 2352 | 3120 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,4LV5H |  | 5,5,4 | 14Dr LV5H | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 11.5 | 23.4 | 27.8 | 1380 | 2808 | 3336 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,3LV5H |  | 4,4,3,3 | 14Dr LV5H | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 11.6 | 23.6 | 28.4 | 1392 | 2832 | 3408 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,5LV5H |  | 5,5,5 | 15Dr LV5H | 1 |  | Frozen Food | 25.5 | -25 | HG 2 Wire | 115 | 12.3 | 23.4 | 29.7 | 1476 | 2808 | 3564 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3LV5H |  | 4,4,4,3 | 15Dr LV5H | 1 |  | Frozen Food | 25.5 | -25 | HG 2 Wire | 115 | 12.4 | 27.4 | 30.2 | 1488 | 3288 | 3624 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3LV5H |  | 5,5,3,3 | 16Dr LV5H | 1 |  | Frozen Food | 27.2 | -25 | HG 2 Wire | 115 | 13.2 | 23.6 | 32.2 | 1584 | 2832 | 3864 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4LV5H |  | 4,4,4,4 | 16Dr LV5H | 1 |  | Frozen Food | 27.2 | -25 | HG 2 Wire | 115 | 13.2 | 31.2 | 32 | 1584 | 3744 | 3840 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,3)3,3LV5H/H1 |  | 5,3)3,3 | 14Dr LV5H/H1 | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 10.5 | 18 | 27.1 | 1260 | 2160 | 3252 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | IV5H ICE CREAM | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
3IV5H |  | 3 | IV5H | 1 |  | Ice Cream | 6 | -25 | HG 2 Wire | 115 | 2.5 | 4 | 6.2 | 300 | 480 | 744 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
4IV5H |  | 4 | IV5H | 1 |  | Ice Cream | 8 | -25 | HG 2 Wire | 115 | 3.3 | 7.8 | 8 | 396 | 936 | 960 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
5IV5H |  | 5 | IV5H | 1 |  | Ice Cream | 10 | -25 | HG 2 Wire | 115 | 4.1 | 7.8 | 9.9 | 492 | 936 | 1188 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
3,3IV5H |  | 3,3 | 6Dr IV5H | 1 |  | Ice Cream | 12 | -25 | HG 2 Wire | 115 | 5 | 8 | 12.4 | 600 | 960 | 1488 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,3IV5H |  | 4,3 | 7Dr IV5H | 1 |  | Ice Cream | 14 | -25 | HG 2 Wire | 115 | 5.8 | 11.8 | 14.2 | 696 | 1416 | 1704 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,4IV5H |  | 4,4 | 8Dr IV5H | 1 |  | Ice Cream | 16 | -25 | HG 2 Wire | 115 | 6.6 | 15.6 | 16 | 792 | 1872 | 1920 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
5,3IV5H |  | 5,3 | 8Dr IV5H | 1 |  | Ice Cream | 16 | -25 | HG 2 Wire | 115 | 6.6 | 11.8 | 16.1 | 792 | 1416 | 1932 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
5,4IV5H |  | 5,4 | 9Dr IV5H | 1 |  | Ice Cream | 18 | -25 | HG 2 Wire | 115 | 7.4 | 15.6 | 17.9 | 888 | 1872 | 2148 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
3,3,3IV5H |  | 3,3,3 | 9Dr IV5H | 1 |  | Ice Cream | 18 | -25 | HG 2 Wire | 115 | 7.5 | 12 | 18.6 | 900 | 1440 | 2232 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
5,5IV5H |  | 5,5 | 10Dr IV5H | 1 |  | Ice Cream | 20 | -25 | HG 2 Wire | 115 | 8.2 | 15.6 | 19.8 | 984 | 1872 | 2376 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,3,3IV5H |  | 4,3,3 | 10Dr IV5H | 1 |  | Ice Cream | 20 | -25 | HG 2 Wire | 115 | 8.3 | 15.8 | 20.4 | 996 | 1896 | 2448 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,3,3IV5H |  | 5,3,3 | 11Dr IV5H | 1 |  | Ice Cream | 22 | -25 | HG 2 Wire | 115 | 9.1 | 15.8 | 22.3 | 1092 | 1896 | 2676 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,3IV5H |  | 4,4,3 | 11Dr IV5H | 1 |  | Ice Cream | 22 | -25 | HG 2 Wire | 115 | 9.1 | 19.6 | 22.2 | 1092 | 2352 | 2664 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,4IV5H |  | 4,4,4 | 12Dr IV5H | 1 |  | Ice Cream | 24 | -25 | HG 2 Wire | 115 | 9.9 | 23.4 | 24 | 1188 | 2808 | 2880 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
5,4,3IV5H |  | 5,4,3 | 12Dr IV5H | 1 |  | Ice Cream | 24 | -25 | HG 2 Wire | 115 | 9.9 | 19.6 | 24.1 | 1188 | 2352 | 2892 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
5,4,4IV5H |  | 5,4,4 | 13Dr IV5H | 1 |  | Ice Cream | 26 | -25 | HG 2 Wire | 115 | 10.7 | 23.4 | 25.9 | 1284 | 2808 | 3108 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
5,5,3IV5H |  | 5,5,3 | 13Dr IV5H | 1 |  | Ice Cream | 26 | -25 | HG 2 Wire | 115 | 10.7 | 19.6 | 26 | 1284 | 2352 | 3120 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
5,5,4IV5H |  | 5,5,4 | 14Dr IV5H | 1 |  | Ice Cream | 28 | -25 | HG 2 Wire | 115 | 11.5 | 23.4 | 27.8 | 1380 | 2808 | 3336 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
4,4,3,3IV5H |  | 4,4,3,3 | 14Dr IV5H | 1 |  | Ice Cream | 28 | -25 | HG 2 Wire | 115 | 11.6 | 23.6 | 28.4 | 1392 | 2832 | 3408 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
5,5,5IV5H |  | 5,5,5 | 15Dr IV5H | 1 |  | Ice Cream | 30 | -25 | HG 2 Wire | 115 | 12.3 | 23.4 | 29.7 | 1476 | 2808 | 3564 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
4,4,4,3IV5H |  | 4,4,4,3 | 15Dr IV5H | 1 |  | Ice Cream | 30 | -25 | HG 2 Wire | 115 | 12.4 | 27.4 | 30.2 | 1488 | 3288 | 3624 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
5,5,3,3IV5H |  | 5,5,3,3 | 16Dr IV5H | 1 |  | Ice Cream | 32 | -25 | HG 2 Wire | 115 | 13.2 | 23.6 | 32.2 | 1584 | 2832 | 3864 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
4,4,4,4IV5H |  | 4,4,4,4 | 16Dr IV5H | 1 |  | Ice Cream | 32 | -25 | HG 2 Wire | 115 | 13.2 | 31.2 | 32 | 1584 | 3744 | 3840 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
|  | LV5HF1 WITH EPR | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
3LV5HF1S |  | 3 | LV5HF1 | 1 |  | Frozen Meat | 4.5 | -15 | HG 2 Wire | 115 | 1.4 | 2.2 | 4.3 | 168 | 264 | 516 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
4LV5HF1S |  | 4 | LV5HF1 | 1 |  | Frozen Meat | 6 | -15 | HG 2 Wire | 115 | 2 | 6.3 | 5.5 | 240 | 756 | 660 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5LV5HF1S |  | 5 | LV5HF1 | 1 |  | Frozen Meat | 7.5 | -15 | HG 2 Wire | 115 | 2.3 | 6.3 | 6.8 | 276 | 756 | 816 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3LV5HF1S |  | 3,3 | 6Dr LV5HF1 | 1 |  | Frozen Meat | 9 | -15 | HG 2 Wire | 115 | 2.8 | 4.4 | 8.6 | 336 | 528 | 1032 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,3LV5HF1S |  | 4,3 | 7Dr LV5HF1 | 1 |  | Frozen Meat | 10.5 | -15 | HG 2 Wire | 115 | 3.4 | 8.5 | 9.8 | 408 | 1020 | 1176 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4,4LV5HF1S |  | 4,4 | 8Dr LV5HF1 | 1 |  | Frozen Meat | 12 | -15 | HG 2 Wire | 115 | 4 | 12.6 | 11 | 480 | 1512 | 1320 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3LV5HF1S |  | 5,3 | 8Dr LV5HF1 | 1 |  | Frozen Meat | 12 | -15 | HG 2 Wire | 115 | 3.7 | 8.5 | 11.1 | 444 | 1020 | 1332 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4LV5HF1S |  | 5,4 | 9Dr LV5HF1 | 1 |  | Frozen Meat | 13.5 | -15 | HG 2 Wire | 115 | 4.3 | 12.6 | 12.3 | 516 | 1512 | 1476 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
3,3,3LV5HF1S |  | 3,3,3 | 9Dr LV5HF1 | 1 |  | Frozen Meat | 13.5 | -15 | HG 2 Wire | 115 | 4.2 | 6.6 | 12.9 | 504 | 792 | 1548 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,5LV5HF1S |  | 5,5 | 10Dr LV5HF1 | 1 |  | Frozen Meat | 15 | -15 | HG 2 Wire | 115 | 4.6 | 12.6 | 13.6 | 552 | 1512 | 1632 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3,3LV5HF1S |  | 4,3,3 | 10Dr LV5HF1 | 1 |  | Frozen Meat | 15 | -15 | HG 2 Wire | 115 | 4.8 | 10.7 | 14.1 | 576 | 1284 | 1692 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3,3LV5HF1S |  | 5,3,3 | 11Dr LV5HF1 | 1 |  | Frozen Meat | 16.5 | -15 | HG 2 Wire | 115 | 5.1 | 10.7 | 15.4 | 612 | 1284 | 1848 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,3LV5HF1S |  | 4,4,3 | 11Dr LV5HF1 | 1 |  | Frozen Meat | 16.5 | -15 | HG 2 Wire | 115 | 5.4 | 14.8 | 15.3 | 648 | 1776 | 1836 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
4,4,4LV5HF1S |  | 4,4,4 | 12Dr LV5HF1 | 1 |  | Frozen Meat | 18 | -15 | HG 2 Wire | 115 | 6 | 18.9 | 16.5 | 720 | 2268 | 1980 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,3LV5HF1S |  | 5,4,3 | 12Dr LV5HF1 | 1 |  | Frozen Meat | 18 | -15 | HG 2 Wire | 115 | 5.7 | 14.8 | 16.6 | 684 | 1776 | 1992 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4,4LV5HF1S |  | 5,4,4 | 13Dr LV5HF1 | 1 |  | Frozen Meat | 19.5 | -15 | HG 2 Wire | 115 | 6.3 | 18.9 | 17.8 | 756 | 2268 | 2136 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3LV5HF1S |  | 5,5,3 | 13Dr LV5HF1 | 1 |  | Frozen Meat | 19.5 | -15 | HG 2 Wire | 115 | 6 | 14.8 | 17.9 | 720 | 1776 | 2148 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4LV5HF1S |  | 5,5,4 | 14Dr LV5HF1 | 1 |  | Frozen Meat | 21 | -15 | HG 2 Wire | 115 | 6.6 | 18.9 | 19.1 | 792 | 2268 | 2292 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,3LV5HF1S |  | 4,4,3,3 | 14Dr LV5HF1 | 1 |  | Frozen Meat | 21 | -15 | HG 2 Wire | 115 | 6.8 | 17 | 19.6 | 816 | 2040 | 2352 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,5LV5HF1S |  | 5,5,5 | 15Dr LV5HF1 | 1 |  | Frozen Meat | 22.5 | -15 | HG 2 Wire | 115 | 6.9 | 18.9 | 20.4 | 828 | 2268 | 2448 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4,3LV5HF1S |  | 4,4,4,3 | 15Dr LV5HF1 | 1 |  | Frozen Meat | 22.5 | -15 | HG 2 Wire | 115 | 7.4 | 21.1 | 20.8 | 888 | 2532 | 2496 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3,3LV5HF1S |  | 5,5,3,3 | 16Dr LV5HF1 | 1 |  | Frozen Meat | 24 | -15 | HG 2 Wire | 115 | 7.4 | 17 | 22.2 | 888 | 2040 | 2664 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
4,4,4,4LV5HF1S |  | 4,4,4,4 | 16Dr LV5HF1 | 1 |  | Frozen Meat | 24 | -15 | HG 2 Wire | 115 | 8 | 25.2 | 22 | 960 | 3024 | 2640 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
|  | LV5HF1 WITH SUCTION STOP | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
3LV5HF1SS |  | 3 | LV5HF1 | 1 |  | Frozen Meat | 4.5 | -15 | HG 2 Wire | 115 | 1.4 | 2.2 | 4.3 | 168 | 264 | 516 | ME14S250 |  | ME14S250 |  |  | 5/8 | 1/2
4LV5HF1SS |  | 4 | LV5HF1 | 1 |  | Frozen Meat | 6 | -15 | HG 2 Wire | 115 | 2 | 6.3 | 5.5 | 240 | 756 | 660 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
5LV5HF1SS |  | 5 | LV5HF1 | 1 |  | Frozen Meat | 7.5 | -15 | HG 2 Wire | 115 | 2.5 | 6.3 | 6.8 | 300 | 756 | 816 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
3,3LV5HF1SS |  | 3,3 | 6Dr LV5HF1 | 1 |  | Frozen Meat | 9 | -15 | HG 2 Wire | 115 | 2.8 | 4.4 | 8.6 | 336 | 528 | 1032 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
4,3LV5HF1SS |  | 4,3 | 7Dr LV5HF1 | 1 |  | Frozen Meat | 10.5 | -15 | HG 2 Wire | 115 | 3.4 | 8.5 | 9.8 | 408 | 1020 | 1176 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
4,4LV5HF1SS |  | 4,4 | 8Dr LV5HF1 | 1 |  | Frozen Meat | 12 | -15 | HG 2 Wire | 115 | 4 | 12.6 | 11 | 480 | 1512 | 1320 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
5,3LV5HF1SS |  | 5,3 | 8Dr LV5HF1 | 1 |  | Frozen Meat | 12 | -15 | HG 2 Wire | 115 | 3.9 | 8.5 | 11.1 | 468 | 1020 | 1332 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
5,4LV5HF1SS |  | 5,4 | 9Dr LV5HF1 | 1 |  | Frozen Meat | 13.5 | -15 | HG 2 Wire | 115 | 4.5 | 12.6 | 12.3 | 540 | 1512 | 1476 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
3,3,3LV5HF1SS |  | 3,3,3 | 9Dr LV5HF1 | 1 |  | Frozen Meat | 13.5 | -15 | HG 2 Wire | 115 | 4.2 | 6.6 | 12.9 | 504 | 792 | 1548 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,5LV5HF1SS |  | 5,5 | 10Dr LV5HF1 | 1 |  | Frozen Meat | 15 | -15 | HG 2 Wire | 115 | 5 | 12.6 | 13.6 | 600 | 1512 | 1632 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,3,3LV5HF1SS |  | 4,3,3 | 10Dr LV5HF1 | 1 |  | Frozen Meat | 15 | -15 | HG 2 Wire | 115 | 4.8 | 10.7 | 14.1 | 576 | 1284 | 1692 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,3,3LV5HF1SS |  | 5,3,3 | 11Dr LV5HF1 | 1 |  | Frozen Meat | 16.5 | -15 | HG 2 Wire | 115 | 5.3 | 10.7 | 15.4 | 636 | 1284 | 1848 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,4,3LV5HF1SS |  | 4,4,3 | 11Dr LV5HF1 | 1 |  | Frozen Meat | 16.5 | -15 | HG 2 Wire | 115 | 5.4 | 14.8 | 15.3 | 648 | 1776 | 1836 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
4,4,4LV5HF1SS |  | 4,4,4 | 12Dr LV5HF1 | 1 |  | Frozen Meat | 18 | -15 | HG 2 Wire | 115 | 6 | 18.9 | 16.5 | 720 | 2268 | 1980 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,4,3LV5HF1SS |  | 5,4,3 | 12Dr LV5HF1 | 1 |  | Frozen Meat | 18 | -15 | HG 2 Wire | 115 | 5.9 | 14.8 | 16.6 | 708 | 1776 | 1992 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
5,4,4LV5HF1SS |  | 5,4,4 | 13Dr LV5HF1 | 1 |  | Frozen Meat | 19.5 | -15 | HG 2 Wire | 115 | 6.5 | 18.9 | 17.8 | 780 | 2268 | 2136 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,3LV5HF1SS |  | 5,5,3 | 13Dr LV5HF1 | 1 |  | Frozen Meat | 19.5 | -15 | HG 2 Wire | 115 | 6.4 | 14.8 | 17.9 | 768 | 1776 | 2148 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,4LV5HF1SS |  | 5,5,4 | 14Dr LV5HF1 | 1 |  | Frozen Meat | 21 | -15 | HG 2 Wire | 115 | 7 | 18.9 | 19.1 | 840 | 2268 | 2292 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,3,3LV5HF1SS |  | 4,4,3,3 | 14Dr LV5HF1 | 1 |  | Frozen Meat | 21 | -15 | HG 2 Wire | 115 | 6.8 | 17 | 19.6 | 816 | 2040 | 2352 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,5LV5HF1SS |  | 5,5,5 | 15Dr LV5HF1 | 1 |  | Frozen Meat | 22.5 | -15 | HG 2 Wire | 115 | 7.5 | 18.9 | 20.4 | 900 | 2268 | 2448 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,4,3LV5HF1SS |  | 4,4,4,3 | 15Dr LV5HF1 | 1 |  | Frozen Meat | 22.5 | -15 | HG 2 Wire | 115 | 7.4 | 21.1 | 20.8 | 888 | 2532 | 2496 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
5,5,3,3LV5HF1SS |  | 5,5,3,3 | 16Dr LV5HF1 | 1 |  | Frozen Meat | 24 | -15 | HG 2 Wire | 115 | 7.8 | 17 | 22.2 | 936 | 2040 | 2664 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
4,4,4,4LV5HF1SS |  | 4,4,4,4 | 16Dr LV5HF1 | 1 |  | Frozen Meat | 24 | -15 | HG 2 Wire | 115 | 8 | 25.2 | 22 | 960 | 3024 | 2640 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
|  | M4A MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8M4A |  | 8' | M4A | 1 |  | MD Fresh Meat | 10.16 | 10 | HG 2 Wire | 115 | 0.6 | 6.3 | 0.4 | 72 | 756 | 48 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 1/2
12M4A |  | 12' | M4A | 1 |  | MD Fresh Meat | 15.26 | 10 | HG 2 Wire | 115 | 0.9 | 10.5 | 0.6 | 108 | 1260 | 72 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
8'8M4A |  | 8'8' | 16' M4A | 1 |  | MD Fresh Meat | 20.32 | 10 | HG 2 Wire | 115 | 1.2 | 12.6 | 0.8 | 144 | 1512 | 96 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
8'12M4A |  | 8'12' | 20' M4A | 1 |  | MD Fresh Meat | 25.42 | 10 | HG 2 Wire | 115 | 1.5 | 16.8 | 1 | 180 | 2016 | 120 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8M4A |  | 8'8'8' | 24' M4A | 1 |  | MD Fresh Meat | 30.48 | 10 | HG 2 Wire | 115 | 1.8 | 18.9 | 1.2 | 216 | 2268 | 144 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
12'12M4A |  | 12'12' | 24' M4A | 1 |  | MD Fresh Meat | 30.52 | 10 | HG 2 Wire | 115 | 1.8 | 21 | 1.2 | 216 | 2520 | 144 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'12M4A |  | 8'8'12' | 28' M4A | 1 |  | MD Fresh Meat | 35.58 | 10 | HG 2 Wire | 115 | 2.1 | 23.1 | 1.4 | 252 | 2772 | 168 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'8M4A |  | 8'8'8'8' | 32' M4A | 1 |  | MD Fresh Meat | 40.64 | 10 | HG 2 Wire | 115 | 2.4 | 25.2 | 1.6 | 288 | 3024 | 192 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'12'12M4A |  | 8'12'12' | 32' M4A | 1 |  | MD Fresh Meat | 40.68 | 10 | HG 2 Wire | 115 | 2.4 | 27.3 | 1.6 | 288 | 3276 | 192 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'8'12M4A |  | 8'8'8'12' | 36' M4A | 1 |  | MD Fresh Meat | 45.74 | 10 | HG 2 Wire | 115 | 2.7 | 29.4 | 1.8 | 324 | 3528 | 216 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
12'12'12M4A |  | 12'12'12' | 36' M4A | 1 |  | MD Fresh Meat | 45.78 | 10 | HG 2 Wire | 115 | 2.7 | 31.5 | 1.8 | 324 | 3780 | 216 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'8'8'8M4A |  | 8'8'8'8'8' | 40' M4A | 1 |  | MD Fresh Meat | 50.8 | 10 | HG 2 Wire | 115 | 3 | 31.5 | 2 | 360 | 3780 | 240 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'12'12M4A |  | 8'8'12'12' | 40' M4A | 1 |  | MD Fresh Meat | 50.84 | 10 | HG 2 Wire | 115 | 3 | 33.6 | 2 | 360 | 4032 | 240 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'8'8'8'12M4A |  | 8'8'8'8'12 | 44' M4A | 1 |  | MD Fresh Meat | 55.9 | 10 | HG 2 Wire | 115 | 3.3 | 35.7 | 2.2 | 396 | 4284 | 264 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
8'12'12'12M4A |  | 8'12'12'12' | 44' M4A | 1 |  | MD Fresh Meat | 55.94 | 10 | HG 2 Wire | 115 | 3.3 | 37.8 | 2.2 | 396 | 4536 | 264 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 7/8
8'8'8'12'12M4A |  | 8'8'8'12'12' | 48' M4A | 1 |  | MD Fresh Meat | 61 | 10 | HG 2 Wire | 115 | 3.6 | 39.9 | 2.4 | 432 | 4788 | 288 | ME14S250 |  | SORIT 20 |  |  | 2 1/8 | 7/8
12'12'12'12M4A |  | 12'12'12'12' | 48' M4A | 1 |  | MD Fresh Meat | 61.04 | 10 | HG 2 Wire | 115 | 3.6 | 42 | 2.4 | 432 | 5040 | 288 | ME14S250 |  | SORIT 20 |  |  | 2 1/8 | 7/8
HZVS1/H3ZV1 COMBINATIONS
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8H3ZV1 |  | 8' | H3ZV1 |  |  | Produce | 7.6 | 20 | Off Cycle | 115 | 0.5 | 4.7 | 0 | 60 | 564 | 0 |  |  | SORIT 12 |  |  | 1/2
12H3ZV1 |  | 12' | H3ZV1 |  |  | Produce | 11.4 | 20 | Off Cycle | 115 | 0.8 | 7 | 0 | 96 | 840 | 0 |  |  | SORIT 12 |  |  | 5/8
8HZVS1 |  | 8' | HZVS1 |  |  | Produce | 6.05 | 20 | Off Cycle | 115 | 1 | 2.1 | 0 | 120 | 252 | 0 |  |  | SORIT 12 |  |  | 1/2
12HZVS1 |  | 12' | HZVS1 |  |  | Produce | 9.08 | 20 | Off Cycle | 115 | 1.5 | 3.2 | 0 | 180 | 384 | 0 |  |  | SORIT 12 |  |  | 5/8
90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8)12'12HZVS1/H3 |  | 8)12'12' | 32' HZVS1/H3 |  |  | Produce | 25.76 | 20 | Off Cycle | 115 | 3.5 | 11.1 | 0 | 420 | 1332 | 0 |  |  | SORIT 12 |  |  | 7/8
8)8'8'12HZVS1/H3 |  | 8)8'8'12' | 36' HZVS1/H3 |  |  | Produce | 28.78 | 20 | Off Cycle | 115 | 4 | 12.1 | 0 | 480 | 1452 | 0 |  |  | SORIT 12 |  |  | 1 1/8
8)8'12'12HZVS1/H3 |  | 8)8'12'12' | 40' HZVS1/H3 |  |  | Produce | 31.81 | 20 | Off Cycle | 115 | 4.5 | 13.2 | 0 | 540 | 1584 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8)12'12'12'HZVS1/H3 |  | 8)12'12'12' | 44' HZVS1/H3 |  |  | Produce | 34.84 | 20 | Off Cycle | 115 | 5 | 14.3 | 0 | 600 | 1716 | 0 |  |  | SORIT 15 |  |  | 1 1/8
|  |  | HZVS1/H3 |  |  | Produce |  | 20 | Off Cycle | 115 |  |  |  | 0 | 0 | 0
|  |  | HZVS1/H3 |  |  | Produce |  | 20 | Off Cycle | 115 |  |  |  | 0 | 0 | 0
|  |  | HZVS1/H3 |  |  | Produce |  | 20 | Off Cycle | 115 |  |  |  | 0 | 0 | 0
|  |  | HZVS1/H3 |  |  | Produce |  | 20 | Off Cycle | 115 |  |  |  | 0 | 0 | 0
|  | TZP PRODUCE ISLAND | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8TZP |  | 8' | TZP |  |  | Produce Table | 5.8 | 20 | Off Cycle | 115 | 2 |  |  | 240 |  |  |  |  | SORIT 12 |  |  | 1/2
12TZP |  | 12' | TZP |  |  | Produce Table | 8.7 | 20 | Off Cycle | 115 | 4 |  |  | 480 |  |  |  |  | SORIT 12 |  |  | 1/2
16TZP |  | 8'8' | TZP |  |  | Produce Table | 11.6 | 20 | Off Cycle | 115 | 4 |  |  | 480 |  |  |  |  | SORIT 12 |  |  | 5/8
24TZP |  | 8'8'8' | TZP |  |  | Produce Table | 17.4 | 20 | Off Cycle | 115 | 6 |  |  | 720 |  |  |  |  | SORIT 12 |  |  | 7/8
32TZP |  | 8'8'8'8' | TZP |  |  | Produce Table | 23.2 | 20 | Off Cycle | 115 | 8 |  |  | 960 |  |  |  |  | SORIT 12 |  |  | 7/8
COPY THIS
|  | 8' | TZP |  |  | Produce Island | 5.80 | 20 |  | 115 | 2 |  |  | 240 | [5 empty] | 5 | 1/2 |  | 3/8
|  | 8' | TZP |  |  | Produce Island | 5.80 | 20 |  | 115 | 2 |  |  | 240 | [5 empty] | 30 | 1/2 |  | 3/8
|  | 8' | TZP |  |  | Produce Island | 5.80 | 20 |  | 115 | 2 |  |  | 240 | [5 empty] | 30 | 1/2 |  | 3/8
[6 empty] | Produce Circ Total | 17.4 | 20 | Off Cycle | 115 | 6 |  |  | 720 |  |  |  |  | SORIT 12 |  |  | 7/8
COPY THIS
|  | 12' | C1RG |  |  | Upper | 4.80 | -20 |  | 115 | 1.8 | 9 | 7.1 | 216 | 1080 | 852 |  |  | -------
|  | 12' | C1RG |  |  | Lower | 3.60 | -25 |  | 115 | 1.1 |  | 0.9 | 132 | 0 | 108 |  |  | -------
|  |  | 12' C1RG |  |  | Circuit Total* | 8.4 | -25 | HG 2 Wire | 115 | 2.9 | 9 | 8 | 348 | 1080 | 960 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
|  | 8' | C1RG |  |  | Upper | 3.20 | -20 |  | 115 | 1.2 | 6.4 | 4.7 | 144 | 768 | 564 |  |  | -------
|  | 8' | C1RG |  |  | Lower | 2.40 | -25 |  | 115 | 0.72 |  | 0.58 | 86.4 | 0 | 69.6 |  |  | -------
|  |  | 8' C1RG |  |  | Circuit Total* | 5.6 | -25 | HG 2 Wire | 115 | 2.9 | 9 | 8 | 348 | 1080 | 960 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
D6R1 REAR LOAD DAIRY
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8D6R1D |  | 8' | D6R1 |  |  | Rear Load Dairy | 10 | 20 | Off Cycle | 115 | 1 | 3.3 |  | 120 | 396 | 0 |  |  | SORIT 12 |  |  | 5/8 | 1/2
12D6R1D |  | 12' | D6R1 |  |  | Rear Load Dairy | 15 | 20 | Off Cycle | 115 | 1.3 | 4.8 |  | 156 | 576 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'8D6R1D |  | 8'8' | 16' D6R1 |  |  | Rear Load Dairy | 20 | 20 | Off Cycle | 115 | 2 | 6.6 |  | 240 | 792 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
8'12D6R1D |  | 8'12' | 20' D6R1 |  |  | Rear Load Dairy | 25 | 20 | Off Cycle | 115 | 2.3 | 8.1 |  | 276 | 972 | 0 |  |  | SORIT 12 |  |  | 1 1/8 | 1/2
8'8'8D6R1D |  | 8'8'8' | 24' D6R1 |  |  | Rear Load Dairy | 30 | 20 | Off Cycle | 115 | 3 | 9.9 |  | 360 | 1188 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
12'12D6R1D |  | 12'12' | 24' D6R1 |  |  | Rear Load Dairy | 30 | 20 | Off Cycle | 115 | 2.6 | 9.6 |  | 312 | 1152 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
8'8'12D6R1D |  | 8'8'12' | 28' D6R1 |  |  | Rear Load Dairy | 35 | 20 | Off Cycle | 115 | 3.3 | 11.4 |  | 396 | 1368 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8D6R1D |  | 8'8'8'8' | 32' D6R1 |  |  | Rear Load Dairy | 40 | 20 | Off Cycle | 115 | 4 | 13.2 |  | 480 | 1584 | 0 |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'12'12D6R1D |  | 8'12'12' | 32' D6R1 |  |  | Rear Load Dairy | 40 | 20 | Off Cycle | 115 | 3.6 | 12.9 |  | 432 | 1548 | 0 |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
8'8'8'12D6R1D |  | 8'8'8'12' | 36' D6R1 |  |  | Rear Load Dairy | 45 | 20 | Off Cycle | 115 | 4.3 | 14.7 |  | 516 | 1764 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
12'12'12D6R1D |  | 12'12'12' | 36' D6R1 |  |  | Rear Load Dairy | 45 | 20 | Off Cycle | 115 | 3.9 | 14.4 |  | 468 | 1728 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'8D6R1D |  | 8'8'8'8'8' | 40' D6R1 |  |  | Rear Load Dairy | 50 | 20 | Off Cycle | 115 | 5 | 16.5 |  | 600 | 1980 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'12'12D6R1D |  | 8'8'12'12' | 40' D6R1 |  |  | Rear Load Dairy | 50 | 20 | Off Cycle | 115 | 4.6 | 16.2 |  | 552 | 1944 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'8'12D6R1D |  | 8'8'8'8'12' | 44' D6R1 |  |  | Rear Load Dairy | 55 | 20 | Off Cycle | 115 | 5.3 | 18 |  | 636 | 2160 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'12'12'12D6R1D |  | 8'12'12'12' | 44' D6R1 |  |  | Rear Load Dairy | 55 | 20 | Off Cycle | 115 | 4.9 | 17.7 |  | 588 | 2124 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
8'8'8'12'12D6R1D |  | 8'8'8'12'12' | 48' D6R1 |  |  | Rear Load Dairy | 60 | 20 | Off Cycle | 115 | 5.6 | 19.5 |  | 672 | 2340 | 0 | [5 empty] | 1 5/8 | 5/8
12'12'12'12D6R1D |  | 12'12'12'12' | 48' D6R1 |  |  | Rear Load Dairy | 60 | 20 | Off Cycle | 115 | 5.2 | 19.2 |  | 624 | 2304 | 0 | [5 empty] | 1 5/8 | 5/8
|  | IV5H1 WITH EPR | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2IV5H1S |  | 2 | IV5H1 | 1 |  | Frozen Food | 3.4 | -25 | HG 2 Wire | 115 | 0.9 | 2.2 | 3.4 | 108 | 264 | 408 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3IV5H1S |  | 3 | IV5H1 | 1 |  | Frozen Food | 5.1 | -25 | HG 2 Wire | 115 | 1.4 | 2.2 | 4.8 | 168 | 264 | 576 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4IV5H1S |  | 4 | IV5H1 | 1 |  | Frozen Food | 6.8 | -25 | HG 2 Wire | 115 | 2 | 6.3 | 6.2 | 240 | 756 | 744 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5IV5H1S |  | 5 | IV5H1 | 1 |  | Frozen Food | 8.5 | -25 | HG 2 Wire | 115 | 2.5 | 6.3 | 7.7 | 300 | 756 | 924 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3IV5H1S |  | 3,3 | 6Dr IV5H1 | 1 |  | Frozen Food | 10.2 | -25 | HG 2 Wire | 115 | 2.8 | 4.4 | 9.6 | 336 | 528 | 1152 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3IV5H1S |  | 4,3 | 7Dr IV5H1 | 1 |  | Frozen Food | 11.9 | -25 | HG 2 Wire | 115 | 3.4 | 8.5 | 11 | 408 | 1020 | 1320 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4IV5H1S |  | 4,4 | 8Dr IV5H1 | 1 |  | Frozen Food | 13.6 | -25 | HG 2 Wire | 115 | 4 | 12.6 | 12.4 | 480 | 1512 | 1488 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,3IV5H1S |  | 5,3 | 8Dr IV5H1 | 1 |  | Frozen Food | 13.6 | -25 | HG 2 Wire | 115 | 3.9 | 8.5 | 12.5 | 468 | 1020 | 1500 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
5,4IV5H1S |  | 5,4 | 9Dr IV5H1 | 1 |  | Frozen Food | 15.3 | -25 | HG 2 Wire | 115 | 4.5 | 12.6 | 13.9 | 540 | 1512 | 1668 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
3,3,3IV5H1S |  | 3,3,3 | 9Dr IV5H1 | 1 |  | Frozen Food | 15.3 | -25 | HG 2 Wire | 115 | 4.2 | 6.6 | 14.4 | 504 | 792 | 1728 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5IV5H1S |  | 5,5 | 10Dr IV5H1 | 1 |  | Frozen Food | 17 | -25 | HG 2 Wire | 115 | 5 | 12.6 | 15.4 | 600 | 1512 | 1848 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3IV5H1S |  | 4,3,3 | 10Dr IV5H1 | 1 |  | Frozen Food | 17 | -25 | HG 2 Wire | 115 | 4.8 | 10.7 | 15.8 | 576 | 1284 | 1896 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3IV5H1S |  | 5,3,3 | 11Dr IV5H1 | 1 |  | Frozen Food | 18.7 | -25 | HG 2 Wire | 115 | 5.3 | 10.7 | 17.3 | 636 | 1284 | 2076 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3IV5H1S |  | 4,4,3 | 11Dr IV5H1 | 1 |  | Frozen Food | 18.7 | -25 | HG 2 Wire | 115 | 5.4 | 14.8 | 17.2 | 648 | 1776 | 2064 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4IV5H1S |  | 4,4,4 | 12Dr IV5H1 | 1 |  | Frozen Food | 20.4 | -25 | HG 2 Wire | 115 | 6 | 18.9 | 18.6 | 720 | 2268 | 2232 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,4,3IV5H1S |  | 5,4,3 | 12Dr IV5H1 | 1 |  | Frozen Food | 20.4 | -25 | HG 2 Wire | 115 | 5.9 | 14.8 | 18.7 | 708 | 1776 | 2244 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,4,4IV5H1S |  | 5,4,4 | 13Dr IV5H1 | 1 |  | Frozen Food | 22.1 | -25 | HG 2 Wire | 115 | 6.5 | 18.9 | 20.1 | 780 | 2268 | 2412 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,3IV5H1S |  | 5,5,3 | 13Dr IV5H1 | 1 |  | Frozen Food | 22.1 | -25 | HG 2 Wire | 115 | 6.4 | 14.8 | 20.2 | 768 | 1776 | 2424 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
5,5,4IV5H1S |  | 5,5,4 | 14Dr IV5H1 | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 7 | 18.9 | 21.6 | 840 | 2268 | 2592 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,3IV5H1S |  | 4,4,3,3 | 14Dr IV5H1 | 1 |  | Frozen Food | 23.8 | -25 | HG 2 Wire | 115 | 6.8 | 17 | 22 | 816 | 2040 | 2640 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,5IV5H1S |  | 5,5,5 | 15Dr IV5H1 | 1 |  | Frozen Food | 25.5 | -25 | HG 2 Wire | 115 | 7.5 | 18.9 | 23.1 | 900 | 2268 | 2772 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3IV5H1S |  | 4,4,4,3 | 15Dr IV5H1 | 1 |  | Frozen Food | 25.5 | -25 | HG 2 Wire | 115 | 7.4 | 21.1 | 23.4 | 888 | 2532 | 2808 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3IV5H1S |  | 5,5,3,3 | 16Dr IV5H1 | 1 |  | Frozen Food | 27.2 | -25 | HG 2 Wire | 115 | 7.8 | 17 | 25 | 936 | 2040 | 3000 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4IV5H1S |  | 4,4,4,4 | 16Dr IV5H1 | 1 |  | Frozen Food | 27.2 | -25 | HG 2 Wire | 115 | 8 | 25.2 | 24.8 | 960 | 3024 | 2976 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,3,2IV5H1S |  | 4,4,3,2 | 13Dr IV5H1 | 1 |  | Frozen Food | 22.1 | -25 | HG 2 Wire | 115 | 6.3 | 17 | 20.6 | 756 | 2040 | 2472 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
|  | L6DL (BEVERAGE, EGGS, & DAIRY) | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L6DL8 |  | 8' | L6DL |  |  | Dairy | 11.4 | 20 | Off Cycle | 120 | 0.6 | 3.4 |  | 72 | 408 | 0 |  |  | SORIT 12 |  |  | 5/8 | 1/2
L6DL12 |  | 12' | L6DL |  |  | Dairy | 17.1 | 20 | Off Cycle | 120 | 0.9 | 6.3 |  | 108 | 756 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
L6DL8'8 |  | 8'8' | 16' L6DL |  |  | Dairy | 22.8 | 20 | Off Cycle | 120 | 1.2 | 6.8 |  | 144 | 816 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
L6DL8'12 |  | 8'12' | 20' L6DL |  |  | Dairy | 28.5 | 20 | Off Cycle | 120 | 1.5 | 9.7 |  | 180 | 1164 | 0 |  |  | SORIT 12 |  |  | 1 1/8 | 1/2
L6DL8'8'8 |  | 8'8'8' | 24' L6DL |  |  | Dairy | 34.2 | 20 | Off Cycle | 120 | 1.8 | 10.2 |  | 216 | 1224 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
L6DL12'12 |  | 12'12' | 24' L6DL |  |  | Dairy | 34.2 | 20 | Off Cycle | 120 | 1.8 | 12.6 |  | 216 | 1512 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
L6DL8'8'12 |  | 8'8'12' | 28' L6DL |  |  | Dairy | 39.9 | 20 | Off Cycle | 120 | 2.1 | 13.1 |  | 252 | 1572 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
L6DL8'8'8'8 |  | 8'8'8'8' | 32' L6DL |  |  | Dairy | 45.6 | 20 | Off Cycle | 120 | 2.4 | 13.6 |  | 288 | 1632 | 0 |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
L6DL8'12'12 |  | 8'12'12' | 32' L6DL |  |  | Dairy | 45.6 | 20 | Off Cycle | 120 | 2.4 | 16 |  | 288 | 1920 | 0 |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
L6DL8'8'8'12 |  | 8'8'8'12' | 36' L6DL |  |  | Dairy | 51.3 | 20 | Off Cycle | 120 | 2.7 | 16.5 |  | 324 | 1980 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DL12'12'12 |  | 12'12'12' | 36' L6DL |  |  | Dairy | 51.3 | 20 | Off Cycle | 120 | 2.7 | 18.9 |  | 324 | 2268 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DL8'8'8'8'8' |  | 8'8'8'8'8' | 40' L6DL |  |  | Beverage | 57 | 20 | Off Cycle | 120 | 3 | 17 |  | 360 | 2040 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DL8'8'12'12 |  | 8'8'12'12' | 40' L6DL |  |  | Beverage | 57 | 20 | Off Cycle | 120 | 3 | 19.4 |  | 360 | 2328 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DL8'8'8'8'12 |  | 8'8'8'8'12' | 44' L6DL |  |  | Beverage | 62.7 | 20 | Off Cycle | 120 | 3.3 | 19.9 |  | 396 | 2388 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DL8'12'12'12 |  | 8'12'12'12' | 44' L6DL |  |  | Beverage | 62.7 | 20 | Off Cycle | 120 | 3.3 | 22.3 |  | 396 | 2676 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DL8'8'8'12'12 |  | 8'8'8'12'12' | 48' L6DL |  |  | Beverage | 68.4 | 20 | Off Cycle | 120 | 3.6 | 22.8 |  | 432 | 2736 | 0 |  |  | SORIT 20 |  |  | 1 5/8 | 5/8
L6DL12'12'12'12 |  | 12'12'12'12' | 48' L6DL |  |  | Beverage | 68.4 | 20 | Off Cycle | 120 | 3.6 | 25.2 |  | 432 | 3024 | 0 |  |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | L6DL DELI MEAT ONLY | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L6DLM8 |  | 8' | L6DL | 1 |  | Deli Meat | 13 | 15 | HG 2 Wire | 120 | 0.6 | 3.4 |  | 72 | 408 | 0 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
L6DLM12 |  | 12' | L6DL | 1 |  | Deli Meat | 19.5 | 15 | HG 2 Wire | 120 | 0.9 | 6.3 |  | 108 | 756 | 0 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L6DLM8'8 |  | 8'8' | 16' L6DL | 1 |  | Deli Meat | 26 | 15 | HG 2 Wire | 120 | 1.2 | 6.8 |  | 144 | 816 | 0 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L6DLM8'12 |  | 8'12' | 20' L6DL | 1 |  | Deli Meat | 32.5 | 15 | HG 2 Wire | 120 | 1.5 | 9.7 |  | 180 | 1164 | 0 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L6DLM8'8'8 |  | 8'8'8' | 24' L6DL | 1 |  | Deli Meat | 39 | 15 | HG 2 Wire | 120 | 1.8 | 10.2 |  | 216 | 1224 | 0 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L6DLM12'12 |  | 12'12' | 24' L6DL | 1 |  | Deli Meat | 39 | 15 | HG 2 Wire | 120 | 1.8 | 12.6 |  | 216 | 1512 | 0 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L6DLM8'8'12 |  | 8'8'12' | 28' L6DL | 1 |  | Deli Meat | 45.5 | 15 | HG 2 Wire | 120 | 2.1 | 13.1 |  | 252 | 1572 | 0 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L6DLM8'8'8'8 |  | 8'8'8'8' | 32' L6DL | 1 |  | Deli Meat | 52 | 15 | HG 2 Wire | 120 | 2.4 | 13.6 |  | 288 | 1632 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLM8'12'12 |  | 8'12'12' | 32' L6DL | 1 |  | Deli Meat | 52 | 15 | HG 2 Wire | 120 | 2.4 | 16 |  | 288 | 1920 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLM8'8'8'12 |  | 8'8'8'12' | 36' L6DL | 1 |  | Deli Meat | 58.5 | 15 | HG 2 Wire | 120 | 2.7 | 16.5 |  | 324 | 1980 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLM12'12'12 |  | 12'12'12' | 36' L6DL | 1 |  | Deli Meat | 58.5 | 15 | HG 2 Wire | 120 | 2.7 | 18.9 |  | 324 | 2268 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLM8'8'8'8'8 |  | 8'8'8'8'8' | 40' L6DL | 1 |  | Deli Meat | 65 | 15 | HG 2 Wire | 120 | 3 | 17 |  | 360 | 2040 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L6DLM8'8'12'12 |  | 8'8'12'12' | 40' L6DL | 1 |  | Deli Meat | 65 | 15 | HG 2 Wire | 120 | 3 | 19.4 |  | 360 | 2328 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L6DLM8'8'8'8'12 |  | 8'8'8'8'12' | 44' L6DL | 1 |  | Deli Meat | 71.5 | 15 | HG 2 Wire | 120 | 3.3 | 19.9 |  | 396 | 2388 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L6DLM8'12'12'12 |  | 8'12'12'12' | 44' L6DL | 1 |  | Deli Meat | 71.5 | 15 | HG 2 Wire | 120 | 3.3 | 22.3 |  | 396 | 2676 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L6DLM8'8'8'12'12 |  | 8'8'8'12'12' | 48' L6DL | 1 |  | Deli Meat | 78 | 15 | HG 2 Wire | 120 | 3.6 | 22.8 |  | 432 | 2736 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L6DLM12'12'12'12 |  | 12'12'12'12' | 48' L6DL | 1 |  | Deli Meat | 78 | 15 | HG 2 Wire | 120 | 3.6 | 25.2 |  | 432 | 3024 | 0 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | DELI CASES | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
LLM8 |  | 8' | LLM |  |  | Cold Deli | 2.8 | 20 | Off Cycle | 120 | 0.4 | 1.2 | 1 | 48 | 144 | 120 |  |  | SORIT 12 |  | 5/8 | 1/2 | 1/2
LLM12 |  | 12' | LLM |  |  | Cold Deli | 4.2 | 20 | Off Cycle | 120 | 0.6 | 1.8 | 1.3 | 72 | 216 | 156 |  |  | SORIT 12 |  | 5/8 | 1/2 | 1/2
LLM16 |  | 8'8' | 16' LLM |  |  | Cold Deli | 5.6 | 20 | Off Cycle | 120 | 0.8 | 2.4 | 2 | 96 | 288 | 240 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
LFW8 |  | 8' | LFW |  |  | Meat Promo | 3.6 | -25 | HG 2 Wire | 120 | 0.4 |  | 1.8 | 48 | 0 | 216 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
LFW12 |  | 12' | LFW |  |  | Meat Promo | 5.4 | -25 | HG 2 Wire | 120 | [6 empty] | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
L3MG8 |  | 8' | L3MG |  |  | Self Serve Deli | 6.8 | 15 | Off Cycle | 120 | 0.4 | 0.6 | 1 | 48 | 72 | 120 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
L3MG12 |  | 12' | L3MG |  |  | Self Serve Deli | 10.2 | 15 | Off Cycle | 120 | 0.6 | 0.9 | 1.4 | 72 | 108 | 168 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
L3MG8'8 |  | 8'8' | 16' L3MG |  |  | Self Serve Deli | 13.6 | 15 | Off Cycle | 120 | 0.8 | 1.2 | 2 | 96 | 144 | 240 |  |  | SORIT 12 |  |  | 7/8 | 1/2
L3MG8/1 |  | 8' | L3MG/1 |  |  | Self Serve Deli | 11.9 | 15 | Off Cycle | 120 | 0.8 | 1.2 | 1.7 | 96 | 144 | 204 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
L3MG8/2 |  | 8' | L3MG/2 |  |  | Self Serve Deli | 17 | 15 | Off Cycle | 120 | 1.2 | 1.8 | 2.4 | 144 | 216 | 288 |  |  | SORIT 12 |  |  | 7/8 | 1/2
L3MG8'8/1 |  | 8'8' | 16' L3MG/1 |  |  | Self Serve Deli | 18.7 | 15 | Off Cycle | 120 | 1.2 | 1.8 | 2.7 | 144 | 216 | 324 |  |  | SORIT 12 |  |  | 7/8
|  |  | WEDGE |  |  |  | 5.1 | 15 | Off Cycle | 120 | 0.4 | 0.6 | 0.7 | 48 | 72 | 84
SSD6 |  | 6' | SSD |  |  | Refrigerated Bakery | 4.3 | 15 | Off Cycle | 120 | 0.4 | 1.2 | 1 | 48 | 144 | 120 |  |  | SORIT 12 |  |  | 1/2 | 1/2
SSD8 |  | 8' | SSD |  |  | Refrigerated Bakery | 5.7 | 15 | Off Cycle | 120 | 0.4 | 1.2 | 1 | 48 | 144 | 120 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
SSD12 |  | 12' | SSD |  |  | Refrigerated Bakery | 8.6 | 15 | Off Cycle | 120 | 0.6 | 1.8 | 1.3 | 72 | 216 | 156 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
SSD8'8 |  | 8'8' | 16' SSD |  |  | Refrigerated Bakery | 11.4 | 15 | Off Cycle | 120 | 0.8 | 2.4 | 2 | 96 | 288 | 240 |  |  | SORIT 12 |  |  | 7/8 | 1/2
SSD8/1 |  | 8' | SSD/1 |  |  | Refrigerated Bakery | 10 | 15 | Off Cycle | 120 | 0.8 | 2.4 | 2 | 96 | 288 | 240 |  |  | SORIT 12 |  | 7/8 | 5/8 | 1/2
SSD8/2 |  | 8' | SSD/2 |  |  | Refrigerated Bakery | 14.3 | 15 | Off Cycle | 120 | 1.2 | 3.6 | 3 | 144 | 432 | 360 |  |  | SORIT 12 |  |  | 7/8 | 1/2
SSD8'8/1 |  | 8'8' | 16' SSD/1 |  |  | Refrigerated Bakery | 15.7 | 15 | Off Cycle | 120 | 1.2 | 3.6 | 3 | 144 | 432 | 360 |  |  | SORIT 12 |  |  | 7/8 | 1/2
SSD6'8 |  | 6'8' | 14' SSD |  |  | Refrigerated Bakery | 10 | 15 | Off Cycle | 120 | 0.8 | 2.4 | 2 | 96 | 288 | 240 |  |  | SORIT 12 |  |  | 7/8 | 1/2
|  |  | WEDGE |  |  |  | 4.3 | 15 |  | 120 | 0.4 | 1.2 | 1 | 48 | 144 | 120
TEMP
PROBE
7X10 |  | 7'X10'X8.5' | AA1-66 |  | EGVE 3/4C | Deli Cooler | 5.9 | 20 | Off Cycle | 120 | 2 | [7 empty] | SORIT 12 |  | 7/8 | 5/8 | 1/2
PREP |  |  |  |  | EGVE |  |  | 30 | Off Cycle | 120 | [8 empty] | SORIT 12
PCOOLER |  |  |  |  | EGVE | Produce Cooler |  | 25 | Off Cycle | 120 | [8 empty] | SORIT 12
DCOOLER |  |  |  |  | EGVE | Dairy Cooler |  | 20 | Off Cycle | 120 | [8 empty] | SORIT 12
MCOOLER |  |  |  |  | EGVE |  |  | 20 | HG 2 Wire | 230/1 | [6 empty] | ME14S250
MFREEZER |  |  |  | 1 | EGVE 3/4ZP | Meat Freezer |  | -15 | HG 2 Wire | 230/1 | [6 empty] | ME14S250 | ME14S250 | ME19S270 |  |  | 7/8 | 5/8
SFREEZER |  |  |  | 1 | EGVE1 1/2ZP | Storage Freezer |  | -15 | HG 2 Wire | 230/1 | [6 empty] | ME14S250 | ME14S250 | ME34S2110 |  | 1 3/8 | 1 3/8 | 5/8
10X15 |  | 10'X15'X8.5' | AG3-140 | 1 | EGVE1 1/2ZP | Bakery Freezer | 12.45 | -15 | HG 2 Wire | 230/1 | 3 | [5 empty] | ME14S250 | ME14S250 | ME19S270 |  | 1 3/8 | 1 1/8 | 5/8
12X15 |  | 12'X15'X8.5 | AG5-180 | 1 | EGVE1 1/2ZP | Ice Cream Freezer | 13.65 | -25 | HG 2 Wire | 230/1 | 5 | [5 empty] | ME14S250 | ME14S250 | ME25S290 |  | 1 3/8 | 1 1/8 | 5/8
|  | L1P PRODUCE | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L1P8 |  | 8' | L1P |  |  | Produce | 3 | 20 | Off Cycle | 120 | 0.4 | 1.1 |  | 48 | 132 |  |  |  | SORIT 12 |  |  | 1/2
L1P12 |  | 12' | L1P |  |  | Produce | 9 | 20 | Off Cycle | 120 | 0.6 | 1.8 |  | 72 | 216 |  |  |  | SORIT 12 |  |  | 5/8
L1P8'8 |  | 8'8' | 16' L1P |  |  | Produce | 6 | 20 | Off Cycle | 120 | 0.8 | 2.2 |  | 96 | 264 |  |  |  | SORIT 12 |  |  | 5/8
L1P8'12 |  | 8'12' | 20' L1P |  |  | Produce | 12 | 20 | Off Cycle | 120 | 1 | 2.9 |  | 120 | 348 |  |  |  | SORIT 12 |  |  | 7/8
L1P8'8'8 |  | 8'8'8' | 24' L1P |  |  | Produce | 9 | 20 | Off Cycle | 120 | 1.2 | 3.3 |  | 144 | 396 |  |  |  | SORIT 12 |  |  | 7/8
L1P12'12 |  | 12'12' | 24' L1P |  |  | Produce | 18 | 20 | Off Cycle | 120 | 1.2 | 3.6 |  | 144 | 432 |  |  |  | SORIT 12 |  |  | 7/8
L1P8'8'12 |  | 8'8'12' | 28' L1P |  |  | Produce | 15 | 20 | Off Cycle | 120 | 1.4 | 4 |  | 168 | 480 |  |  |  | SORIT 12 |  |  | 7/8
L1P8'8'8'8 |  | 8'8'8'8' | 32' L1P |  |  | Produce | 12 | 20 | Off Cycle | 120 | 1.6 | 4.4 |  | 192 | 528 |  |  |  | SORIT 12 |  |  | 1 1/8
L1P8'12'12 |  | 8'12'12' | 32' L1P |  |  | Produce | 21 | 20 | Off Cycle | 120 | 1.6 | 4.7 |  | 192 | 564 |  |  |  | SORIT 12 |  |  | 1 1/8
L1P8'8'8'12 |  | 8'8'8'12' | 36' L1P |  |  | Produce | 18 | 20 | Off Cycle | 120 | 1.8 | 5.1 |  | 216 | 612 |  |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
L1P12'12'12 |  | 12'12'12' | 36' L1P |  |  | Produce | 27 | 20 | Off Cycle | 120 | 1.8 | 5.4 |  | 216 | 648 |  |  |  | SORIT 12 |  |  | 1 1/8 | 5/8
L1P8'8'8'8'8 |  | 8'8'8'8'8' | 40' L1P |  |  | Produce | 15 | 20 | Off Cycle | 120 | 2 | 5.5 |  | 240 | 660 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
L1P8'8'12'12 |  | 8'8'12'12' | 40' L1P |  |  | Produce | 24 | 20 | Off Cycle | 120 | 2 | 5.8 |  | 240 | 696 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
L1P8'8'8'8'12 |  | 8'8'8'8'12' | 44' L1P |  |  | Produce | 21 | 20 | Off Cycle | 120 | 2.2 | 6.2 |  | 264 | 744 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
L1P8'12'12'12 |  | 8'12'12'12' | 44' L1P |  |  | Produce | 30 | 20 | Off Cycle | 120 | 2.2 | 6.5 |  | 264 | 780 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
L1P8'8'8'12'12 |  | 8'8'8'12'12' | 48' L1P |  |  | Produce | 27 | 20 | Off Cycle | 120 | 2.4 | 6.9 |  | 288 | 828 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
L1P12'12'12'12 |  | 12'12'12'12' | 48' L1P |  |  | Produce | 36 | 20 | Off Cycle | 120 | 2.4 | 7.2 |  | 288 | 864 |  |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | L4M MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L4M8 |  | 8' | L4M | 1 |  | MD Fresh Meat | 11 | 15 | HG 2 Wire | 120 | 0.6 | 2.5 | 0.3 | 72 | 300 | 36 | ME14S250 |  | SORIT 12 |  |  | 7/8
L4M12 |  | 12' | L4M | 1 |  | MD Fresh Meat | 16.5 | 15 | HG 2 Wire | 120 | 0.9 | 3.9 | 0.5 | 108 | 468 | 60 | ME14S250 |  | SORIT 12 |  |  | 7/8
L4M8'8 |  | 8'8' | 16' L4M | 1 |  | MD Fresh Meat | 22 | 15 | HG 2 Wire | 120 | 1.2 | 5 | 0.6 | 144 | 600 | 72 | ME14S250 |  | SORIT 12 |  |  | 1 1/8
L4M8'12 |  | 8'12' | 20' L4M | 1 |  | MD Fresh Meat | 27.5 | 15 | HG 2 Wire | 120 | 1.5 | 6.4 | 0.8 | 180 | 768 | 96 | ME14S250 |  | SORIT 15 |  |  | 1 1/8
L4M8'8'8 |  | 8'8'8' | 24' L4M | 1 |  | MD Fresh Meat | 33 | 15 | HG 2 Wire | 120 | 1.8 | 7.5 | 0.9 | 216 | 900 | 108 | ME14S250 |  | SORIT 15 |  |  | 1 3/8
L4M12'12 |  | 12'12' | 24' L4M | 1 |  | MD Fresh Meat | 33 | 15 | HG 2 Wire | 120 | 1.8 | 7.8 | 1 | 216 | 936 | 120 | ME14S250 |  | SORIT 15 |  |  | 1 3/8
L4M8'8'12 |  | 8'8'12' | 28' L4M | 1 |  | MD Fresh Meat | 38.5 | 15 | HG 2 Wire | 120 | 2.1 | 8.9 | 1.1 | 252 | 1068 | 132 | ME14S250 |  | SORIT 20 |  |  | 1 3/8
L4M8'8'8'8 |  | 8'8'8'8' | 32' L4M | 1 |  | MD Fresh Meat | 44 | 15 | HG 2 Wire | 120 | 2.4 | 10 | 1.2 | 288 | 1200 | 144 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M8'12'12 |  | 8'12'12' | 32' L4M | 1 |  | MD Fresh Meat | 44 | 15 | HG 2 Wire | 120 | 2.4 | 10.3 | 1.3 | 288 | 1236 | 156 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M8'8'8'12 |  | 8'8'8'12' | 36' L4M | 1 |  | MD Fresh Meat | 49.5 | 15 | HG 2 Wire | 120 | 2.7 | 11.4 | 1.4 | 324 | 1368 | 168 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M12'12'12 |  | 12'12'12' | 36' L4M | 1 |  | MD Fresh Meat | 49.5 | 15 | HG 2 Wire | 120 | 2.7 | 11.7 | 1.5 | 324 | 1404 | 180 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M8'8'8'8'8 |  | 8'8'8'8'8' | 40' L4M | 1 |  | MD Fresh Meat | 55 | 15 | HG 2 Wire | 120 | 3 | 12.5 | 1.5 | 360 | 1500 | 180 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M8'8'12'12 |  | 8'8'12'12' | 40' L4M | 1 |  | MD Fresh Meat | 55 | 15 | HG 2 Wire | 120 | 3 | 12.8 | 1.6 | 360 | 1536 | 192 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M8'8'8'8'12 |  | 8'8'8'8'12' | 44' L4M | 1 |  | MD Fresh Meat | 60.5 | 15 | HG 2 Wire | 120 | 3.3 | 13.9 | 1.7 | 396 | 1668 | 204 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M8'12'12'12 |  | 8'12'12'12' | 44' L4M | 1 |  | MD Fresh Meat | 60.5 | 15 | HG 2 Wire | 120 | 3.3 | 14.2 | 1.8 | 396 | 1704 | 216 | ME14S250 |  | SORIT 20 |  |  | 1 5/8
L4M8'8'8'12'12 |  | 8'8'8'12'12' | 48' L4M | 1 |  | MD Fresh Meat | 66 | 15 | HG 2 Wire | 120 | 3.6 | 15.3 | 1.9 | 432 | 1836 | 228 | ME14S250 |  | SORIT 20 |  |  | 2 1/8
L4M12'12'12'12 |  | 12'12'12'12' | 48' L4M | 1 |  | MD Fresh Meat | 66 | 15 | HG 2 Wire | 120 | 3.6 | 15.6 | 2 | 432 | 1872 | 240 | ME14S250 |  | SORIT 20 |  |  | 2 1/8
FOR USE WITH +10 SUCTION AND +115/+110 CONDENSING TEMPS
|  | LM FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
LM8 |  | 8' | LM | 1 |  | Fresh Meat | 3.8 | 15 | HG 2 Wire | 120 | 0.4 |  | 0.3 | 48 | 0 | 36 | ME14S250 |  | SORIT 12 |  |  | 1/2 | 5/8
LM12 |  | 12' | LM | 1 |  | Fresh Meat | 5.7 | 15 | HG 2 Wire | 120 | 0.6 |  | 0.4 | 72 | 0 | 48 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
LM8'8 |  | 8'8' | 16' LM | 1 |  | Fresh Meat | 7.6 | 15 | HG 2 Wire | 120 | 0.8 | 0 | 0.6 | 96 | 0 | 72 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 5/8
LM8'12 |  | 8'12' | 20' LM | 1 |  | Fresh Meat | 9.5 | 15 | HG 2 Wire | 120 | 1 | 0 | 0.7 | 120 | 0 | 84 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM8'8'8 |  | 8'8'8' | 24' LM | 1 |  | Fresh Meat | 11.4 | 15 | HG 2 Wire | 120 | 1.2 | 0 | 0.9 | 144 | 0 | 108 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM12'12 |  | 12'12' | 24' LM | 1 |  | Fresh Meat | 11.4 | 15 | HG 2 Wire | 120 | 1.2 | 0 | 0.8 | 144 | 0 | 96 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM8'8'12 |  | 8'8'12' | 28' LM | 1 |  | Fresh Meat | 13.3 | 15 | HG 2 Wire | 120 | 1.4 | 0 | 1 | 168 | 0 | 120 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM8'8'8'8 |  | 8'8'8'8' | 32' LM | 1 |  | Fresh Meat | 15.2 | 15 | HG 2 Wire | 120 | 1.6 | 0 | 1.2 | 192 | 0 | 144 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM8'12'12 |  | 8'12'12' | 32' LM | 1 |  | Fresh Meat | 15.2 | 15 | HG 2 Wire | 120 | 1.6 | 0 | 1.1 | 192 | 0 | 132 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM8'8'8'12 |  | 8'8'8'12' | 36' LM | 1 |  | Fresh Meat | 17.1 | 15 | HG 2 Wire | 120 | 1.8 | 0 | 1.3 | 216 | 0 | 156 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM12'12'12 |  | 12'12'12' | 36' LM | 1 |  | Fresh Meat | 17.1 | 15 | HG 2 Wire | 120 | 1.8 | 0 | 1.2 | 216 | 0 | 144 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
LM8'8'8'8'8 |  | 8'8'8'8'8' | 40' LM | 1 |  | Fresh Meat | 19 | 15 | HG 2 Wire | 120 | 2 | 0 | 1.5 | 240 | 0 | 180 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
LM8'8'12'12 |  | 8'8'12'12' | 40' LM | 1 |  | Fresh Meat | 19 | 15 | HG 2 Wire | 120 | 2 | 0 | 1.4 | 240 | 0 | 168 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
LM8'8'8'8'12 |  | 8'8'8'8'12' | 44' LM | 1 |  | Fresh Meat | 20.9 | 15 | HG 2 Wire | 120 | 2.2 | 0 | 1.6 | 264 | 0 | 192 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
LM8'12'12'12 |  | 8'12'12'12' | 44' LM | 1 |  | Fresh Meat | 20.9 | 15 | HG 2 Wire | 120 | 2.2 | 0 | 1.5 | 264 | 0 | 180 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
LM8'8'8'12'12 |  | 8'8'8'12'12' | 48' LM | 1 |  | Fresh Meat | 22.8 | 15 | HG 2 Wire | 120 | 2.4 | 0 | 1.7 | 288 | 0 | 204 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
LM12'12'12'12 |  | 12'12'12'12' | 48' LM | 1 |  | Fresh Meat | 22.8 | 15 | HG 2 Wire | 120 | 2.4 | 0 | 1.6 | 288 | 0 | 192 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
LM8'8'12'12'12' |  | 8'8'12'12'12' | 52' LM | 1 |  | Fresh Meat | 24.7 | 15 | HG 2 Wire | 120 | 2.6 | 0 | 1.8 | 312 | 0 | 216 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
52 |  |  | 52' LM |  |  | Fresh Meat |  | 15 | HG 2 Wire | 120 |  |  |  | 0 | 0 | 0 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
LM8'12'12'12'12 |  | 8'12'12'12'12 | 56'LM | 1 |  | Fresh Meat | 26.6 | 15 | HG 2 Wire | 120 | 2.8 | 0 | 1.9 | 336 | 0 | 228 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
56 |  |  | LM |  |  | Fresh Meat | 30.52 | 15 | HG 2 Wire | 120 |  |  |  | 0 | 0 | 0 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
|  | L5FG WITH EPR | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L5FG2S |  | 2 | L5FG | 1 |  | Frozen Food | 3.3 | -16 | HG 2 Wire | 120 | 0.9 | 2.2 | 3.2 | 108 | 264 | 384 | ME14S250 |  | SORIT 12 |  |  | 1/2 | 1/2
L5FG3S |  | 3 | L5FG | 1 |  | Frozen Food | 4.9 | -16 | HG 2 Wire | 120 | 1.3 | 2.9 | 4.7 | 156 | 348 | 564 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
L5FG4S |  | 4 | L5FG | 1 |  | Frozen Food | 6.6 | -16 | HG 2 Wire | 120 | 1.5 | 3.7 | 6.2 | 180 | 444 | 744 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L5FG5S |  | 5 | L5FG | 1 |  | Frozen Food | 8.2 | -16 | HG 2 Wire | 120 | 2 | 4.3 | 7.8 | 240 | 516 | 936 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L5FG3,3S |  | 3,3 | 6Dr L5FG | 1 |  | Frozen Food | 9.8 | -16 | HG 2 Wire | 120 | 2.6 | 5.8 | 9.4 | 312 | 696 | 1128 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L5FG4,3S |  | 4,3 | 7Dr L5FG | 1 |  | Frozen Food | 11.5 | -16 | HG 2 Wire | 120 | 2.8 | 6.6 | 10.9 | 336 | 792 | 1308 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L5FG4,4S |  | 4,4 | 8Dr L5FG | 1 |  | Frozen Food | 13.2 | -16 | HG 2 Wire | 120 | 3 | 7.4 | 12.4 | 360 | 888 | 1488 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FG5,3S |  | 5,3 | 8Dr L5FG | 1 |  | Frozen Food | 13.1 | -16 | HG 2 Wire | 120 | 3.3 | 7.2 | 12.5 | 396 | 864 | 1500 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FG5,4S |  | 5,4 | 9Dr L5FG | 1 |  | Frozen Food | 14.8 | -16 | HG 2 Wire | 120 | 3.5 | 8 | 14 | 420 | 960 | 1680 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FG3,3,3S |  | 3,3,3 | 9Dr L5FG | 1 |  | Frozen Food | 14.7 | -16 | HG 2 Wire | 120 | 3.9 | 8.7 | 14.1 | 468 | 1044 | 1692 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FG5,5S |  | 5,5 | 10Dr L5FG | 1 |  | Frozen Food | 16.4 | -16 | HG 2 Wire | 120 | 4 | 8.6 | 15.6 | 480 | 1032 | 1872 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FG4,3,3S |  | 4,3,3 | 10Dr L5FG | 1 |  | Frozen Food | 16.4 | -16 | HG 2 Wire | 120 | 4.1 | 9.5 | 15.6 | 492 | 1140 | 1872 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FG5,3,3S |  | 5,3,3 | 11Dr L5FG | 1 |  | Frozen Food | 18 | -16 | HG 2 Wire | 120 | 4.6 | 10.1 | 17.2 | 552 | 1212 | 2064 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L5FG4,4,3S |  | 4,4,3 | 11Dr L5FG | 1 |  | Frozen Food | 18.1 | -16 | HG 2 Wire | 120 | 4.3 | 10.3 | 17.1 | 516 | 1236 | 2052 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L5FG4,4,4S |  | 4,4,4 | 12Dr L5FG | 1 |  | Frozen Food | 19.8 | -16 | HG 2 Wire | 120 | 4.5 | 11.1 | 18.6 | 540 | 1332 | 2232 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L5FG5,4,3S |  | 5,4,3 | 12Dr L5FG | 1 |  | Frozen Food | 19.7 | -16 | HG 2 Wire | 120 | 4.8 | 10.9 | 18.7 | 576 | 1308 | 2244 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L5FG5,4,4S |  | 5,4,4 | 13Dr L5FG | 1 |  | Frozen Food | 21.4 | -16 | HG 2 Wire | 120 | 5 | 11.7 | 20.2 | 600 | 1404 | 2424 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FG5,5,3S |  | 5,5,3 | 13Dr L5FG | 1 |  | Frozen Food | 21.3 | -16 | HG 2 Wire | 120 | 5.3 | 11.5 | 20.3 | 636 | 1380 | 2436 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FG5,5,4S |  | 5,5,4 | 14Dr L5FG | 1 |  | Frozen Food | 23 | -16 | HG 2 Wire | 120 | 5.5 | 12.3 | 21.8 | 660 | 1476 | 2616 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FG4,4,3,3S |  | 4,4,3,3 | 14Dr L5FG | 1 |  | Frozen Food | 23 | -16 | HG 2 Wire | 120 | 5.6 | 13.2 | 21.8 | 672 | 1584 | 2616 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FG5,5,5S |  | 5,5,5 | 15Dr L5FG | 1 |  | Frozen Food | 24.6 | -16 | HG 2 Wire | 120 | 6 | 12.9 | 23.4 | 720 | 1548 | 2808 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FG4,4,4,3S |  | 4,4,4,3 | 15Dr L5FG | 1 |  | Frozen Food | 24.7 | -16 | HG 2 Wire | 120 | 5.8 | 14 | 23.3 | 696 | 1680 | 2796 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FG5,5,3,3S |  | 5,5,3,3 | 16Dr L5FG | 1 |  | Frozen Food | 26.2 | -16 | HG 2 Wire | 120 | 6.6 | 14.4 | 25 | 792 | 1728 | 3000 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L5FG4,4,4,4S |  | 4,4,4,4 | 16Dr L5FG | 1 |  | Frozen Food | 26.4 | -16 | HG 2 Wire | 120 | 6 | 14.8 | 24.8 | 720 | 1776 | 2976 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L5FG4,3,2S | * | 4,3,2 | 9Dr L5FG | 1 |  | Frozen Food | 14.5 | -16 | HG 2 Wire | 120 | 3.7 | 8.8 | 14.1 | 444 | 1056 | 1692 | ME14S250 |  | SORIT 20 |  |  | 1 1/8 | 5/8
L5FG5,3,2S | * | 5,3,2 | 10Dr L5FG | 1 |  | Frozen Food | 15 | -16 | HG 2 Wire | 120 | 4.2 | 9.4 | 15.7 | 504 | 1128 | 1884 | ME14S250 |  | SORIT 20 |  |  | 1 1/8 | 5/8
L5FG5,3,3,3S |  | 5,3,3,3 | 14Dr L5FG | 1 |  | Frozen Food | 22.9 | -16 | HG 2 Wire | 120 | 5.9 | 13 | 21.9 | 708 | 1560 | 2628 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FG4,4,3,2S |  | 4,4,3,2 | 13Dr L5FG | 1 |  | Frozen Food | 21.4 | -16 | HG 2 Wire | 120 | 5.2 | 12.5 | 20.3 | 624 | 1500 | 2436 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
|  | L5FG WITH SUCTION STOP | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L5FG2SS |  | 2 | L5FG | 1 |  | Frozen Food | 3.3 | -16 | HG 2 Wire | 120 | 0.9 | 2.2 | 3.2 | 108 | 264 | 384 | ME14S250 |  | ME14S250 |  |  | 1/2 | 1/2
L5FG3SS |  | 3 | L5FG | 1 |  | Frozen Food | 4.9 | -16 | HG 2 Wire | 120 | 1.3 | 2.9 | 4.7 | 156 | 348 | 564 | ME14S250 |  | ME14S250 |  |  | 5/8 | 1/2
L5FG4SS |  | 4 | L5FG | 1 |  | Frozen Food | 6.6 | -16 | HG 2 Wire | 120 | 1.5 | 3.7 | 6.2 | 180 | 444 | 744 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
L5FG5SS |  | 5 | L5FG | 1 |  | Frozen Food | 8.2 | -16 | HG 2 Wire | 120 | 2 | 4.3 | 7.8 | 240 | 516 | 936 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
L5FG3,3SS |  | 3,3 | 6Dr L5FG | 1 |  | Frozen Food | 9.8 | -16 | HG 2 Wire | 120 | 2.6 | 5.8 | 9.4 | 312 | 696 | 1128 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
L5FG4,3SS |  | 4,3 | 7Dr L5FG | 1 |  | Frozen Food | 11.5 | -16 | HG 2 Wire | 120 | 2.8 | 6.6 | 10.9 | 336 | 792 | 1308 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
L5FG4,4SS |  | 4,4 | 8Dr L5FG | 1 |  | Frozen Food | 13.2 | -16 | HG 2 Wire | 120 | 3 | 7.4 | 12.4 | 360 | 888 | 1488 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
L5FG5,3SS |  | 5,3 | 8Dr L5FG | 1 |  | Frozen Food | 13.1 | -16 | HG 2 Wire | 120 | 3.3 | 7.2 | 12.5 | 396 | 864 | 1500 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
L5FG5,4SS |  | 5,4 | 9Dr L5FG | 1 |  | Frozen Food | 14.8 | -16 | HG 2 Wire | 120 | 3.5 | 8 | 14 | 420 | 960 | 1680 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG3,3,3SS |  | 3,3,3 | 9Dr L5FG | 1 |  | Frozen Food | 14.7 | -16 | HG 2 Wire | 120 | 3.9 | 8.7 | 14.1 | 468 | 1044 | 1692 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG5,5SS |  | 5,5 | 10Dr L5FG | 1 |  | Frozen Food | 16.4 | -16 | HG 2 Wire | 120 | 4 | 8.6 | 15.6 | 480 | 1032 | 1872 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG4,3,3SS |  | 4,3,3 | 10Dr L5FG | 1 |  | Frozen Food | 16.4 | -16 | HG 2 Wire | 120 | 4.1 | 9.5 | 15.6 | 492 | 1140 | 1872 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG5,3,3SS |  | 5,3,3 | 11Dr L5FG | 1 |  | Frozen Food | 18 | -16 | HG 2 Wire | 120 | 4.6 | 10.1 | 17.2 | 552 | 1212 | 2064 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG4,4,3SS |  | 4,4,3 | 11Dr L5FG | 1 |  | Frozen Food | 18.1 | -16 | HG 2 Wire | 120 | 4.3 | 10.3 | 17.1 | 516 | 1236 | 2052 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG4,4,4SS |  | 4,4,4 | 12Dr L5FG | 1 |  | Frozen Food | 19.8 | -16 | HG 2 Wire | 120 | 4.5 | 11.1 | 18.6 | 540 | 1332 | 2232 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG5,4,3SS |  | 5,4,3 | 12Dr L5FG | 1 |  | Frozen Food | 19.7 | -16 | HG 2 Wire | 120 | 4.8 | 10.9 | 18.7 | 576 | 1308 | 2244 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG5,4,4SS |  | 5,4,4 | 13Dr L5FG | 1 |  | Frozen Food | 21.4 | -16 | HG 2 Wire | 120 | 5 | 11.7 | 20.2 | 600 | 1404 | 2424 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG5,5,3SS |  | 5,5,3 | 13Dr L5FG | 1 |  | Frozen Food | 21.3 | -16 | HG 2 Wire | 120 | 5.3 | 11.5 | 20.3 | 636 | 1380 | 2436 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG5,5,4SS |  | 5,5,4 | 14Dr L5FG | 1 |  | Frozen Food | 23 | -16 | HG 2 Wire | 120 | 5.5 | 12.3 | 21.8 | 660 | 1476 | 2616 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG4,4,3,3SS |  | 4,4,3,3 | 14Dr L5FG | 1 |  | Frozen Food | 23 | -16 | HG 2 Wire | 120 | 5.6 | 13.2 | 21.8 | 672 | 1584 | 2616 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG5,5,5SS |  | 5,5,5 | 15Dr L5FG | 1 |  | Frozen Food | 24.6 | -16 | HG 2 Wire | 120 | 6 | 12.9 | 23.4 | 720 | 1548 | 2808 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG4,4,4,3SS |  | 4,4,4,3 | 15Dr L5FG | 1 |  | Frozen Food | 24.7 | -16 | HG 2 Wire | 120 | 5.8 | 14 | 23.3 | 696 | 1680 | 2796 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG5,5,3,3SS |  | 5,5,3,3 | 16Dr L5FG | 1 |  | Frozen Food | 26.2 | -16 | HG 2 Wire | 120 | 6.6 | 14.4 | 25 | 792 | 1728 | 3000 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG4,4,4,4SS |  | 4,4,4,4 | 16Dr L5FG | 1 |  | Frozen Food | 26.4 | -16 | HG 2 Wire | 120 | 6 | 14.8 | 24.8 | 720 | 1776 | 2976 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FG4,3,2SS |  | 4,3,2 | 9Dr L5FG | 1 |  | Frozen Food | 13.5 | -16 | HG 2 Wire | 120 | 3.7 | 8.8 | 14.1 | 444 | 1056 | 1692 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG5,3,2SS |  | 5,3,2 | 10Dr L5FG | 1 |  | Frozen Food | 15 | -16 | HG 2 Wire | 120 | 4.2 | 9.4 | 15.7 | 504 | 1128 | 1884 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FG5,3,3,3SS |  | 5,3,3,3 | 14Dr L5FG | 1 |  | Frozen Food | 22.9 | -16 | HG 2 Wire | 120 | 5.9 | 13 | 21.9 | 708 | 1560 | 2628 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
|  | L5FG WITH SUCTION STOP |  | ICE CREAM | [13 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L5FGI2SS |  | 2 | L5FG | 1 |  | Ice Cream | 3.5 | -23 | HG 2 Wire | 120 | 0.9 | 2.2 | 3.2 | 108 | 264 | 384 | ME14S250 |  | ME14S250 |  |  | 5/8 | 1/2
L5FGI3SS |  | 3 | L5FG | 1 |  | Ice Cream | 5.3 | -23 | HG 2 Wire | 120 | 1.3 | 2.9 | 4.7 | 156 | 348 | 564 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
L5FGI4SS |  | 4 | L5FG | 1 |  | Ice Cream | 7 | -23 | HG 2 Wire | 120 | 1.5 | 3.7 | 6.2 | 180 | 444 | 744 | ME14S250 |  | ME14S250 |  |  | 7/8 | 5/8
L5FGI5SS |  | 5 | L5FG | 1 |  | Ice Cream | 8.8 | -23 | HG 2 Wire | 120 | 2 | 4.3 | 7.8 | 240 | 516 | 936 | ME14S250 |  | ME19S270 |  |  | 7/8 | 5/8
L5FGI3,3SS |  | 3,3 | 6Dr L5FG | 1 |  | Ice Cream | 10.6 | -23 | HG 2 Wire | 120 | 2.6 | 5.8 | 9.4 | 312 | 696 | 1128 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
L5FGI4,3SS |  | 4,3 | 7Dr L5FG | 1 |  | Ice Cream | 12.3 | -23 | HG 2 Wire | 120 | 2.8 | 6.6 | 10.9 | 336 | 792 | 1308 | ME14S250 |  | ME19S270 |  |  | 1 1/8 | 5/8
L5FGI4,4SS |  | 4,4 | 8Dr L5FG | 1 |  | Ice Cream | 14 | -23 | HG 2 Wire | 120 | 3 | 7.4 | 12.4 | 360 | 888 | 1488 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FGI5,3SS |  | 5,3 | 8Dr L5FG | 1 |  | Ice Cream | 14.1 | -23 | HG 2 Wire | 120 | 3.3 | 7.2 | 12.5 | 396 | 864 | 1500 | ME14S250 |  | ME25S290 |  |  | 1 1/8 | 5/8
L5FGI5,4SS |  | 5,4 | 9Dr L5FG | 1 |  | Ice Cream | 15.8 | -23 | HG 2 Wire | 120 | 3.5 | 8 | 14 | 420 | 960 | 1680 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
L5FGI3,3,3SS |  | 3,3,3 | 9Dr L5FG | 1 |  | Ice Cream | 15.9 | -23 | HG 2 Wire | 120 | 3.9 | 8.7 | 14.1 | 468 | 1044 | 1692 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
L5FGI5,5SS |  | 5,5 | 10Dr L5FG | 1 |  | Ice Cream | 17.6 | -23 | HG 2 Wire | 120 | 4 | 8.6 | 15.6 | 480 | 1032 | 1872 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
L5FGI4,3,3SS |  | 4,3,3 | 10Dr L5FG | 1 |  | Ice Cream | 17.6 | -23 | HG 2 Wire | 120 | 4.1 | 9.5 | 15.6 | 492 | 1140 | 1872 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
L5FGI5,3,3SS |  | 5,3,3 | 11Dr L5FG | 1 |  | Ice Cream | 19.4 | -23 | HG 2 Wire | 120 | 4.6 | 10.1 | 17.2 | 552 | 1212 | 2064 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
L5FGI4,4,3SS |  | 4,4,3 | 11Dr L5FG | 1 |  | Ice Cream | 19.3 | -23 | HG 2 Wire | 120 | 4.3 | 10.3 | 17.1 | 516 | 1236 | 2052 | ME14S250 |  | ME25S290 |  |  | 1 3/8 | 5/8
L5FGI4,4,4SS |  | 4,4,4 | 12Dr L5FG | 1 |  | Ice Cream | 21 | -23 | HG 2 Wire | 120 | 4.5 | 11.1 | 18.6 | 540 | 1332 | 2232 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FGI5,4,3SS |  | 5,4,3 | 12Dr L5FG | 1 |  | Ice Cream | 21.1 | -23 | HG 2 Wire | 120 | 4.8 | 10.9 | 18.7 | 576 | 1308 | 2244 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FGI5,4,4SS |  | 5,4,4 | 13Dr L5FG | 1 |  | Ice Cream | 22.8 | -23 | HG 2 Wire | 120 | 5 | 11.7 | 20.2 | 600 | 1404 | 2424 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FGI5,5,3SS |  | 5,5,3 | 13Dr L5FG | 1 |  | Ice Cream | 22.9 | -23 | HG 2 Wire | 120 | 5.3 | 11.5 | 20.3 | 636 | 1380 | 2436 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
L5FGI5,5,4SS |  | 5,5,4 | 14Dr L5FG | 1 |  | Ice Cream | 24.6 | -23 | HG 2 Wire | 120 | 5.5 | 12.3 | 21.8 | 660 | 1476 | 2616 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
L5FGI4,4,3,3SS |  | 4,4,3,3 | 14Dr L5FG | 1 |  | Ice Cream | 24.6 | -23 | HG 2 Wire | 120 | 5.6 | 13.2 | 21.8 | 672 | 1584 | 2616 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
L5FGI5,5,5SS |  | 5,5,5 | 15Dr L5FG | 1 |  | Ice Cream | 26.4 | -23 | HG 2 Wire | 120 | 6 | 12.9 | 23.4 | 720 | 1548 | 2808 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
L5FGI4,4,4,3SS |  | 4,4,4,3 | 15Dr L5FG | 1 |  | Ice Cream | 26.3 | -23 | HG 2 Wire | 120 | 5.8 | 14 | 23.3 | 696 | 1680 | 2796 | ME14S250 |  | ME34S2110 |  |  | 1 5/8 | 5/8
L5FGI5,5,3,3SS |  | 5,5,3,3 | 16Dr L5FG | 1 |  | Ice Cream | 28.2 | -23 | HG 2 Wire | 120 | 6.6 | 14.4 | 25 | 792 | 1728 | 3000 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
L5FGI4,4,4,4SS |  | 4,4,4,4 | 16Dr L5FG | 1 |  | Ice Cream | 28 | -23 | HG 2 Wire | 120 | 6 | 14.8 | 24.8 | 720 | 1776 | 2976 | ME14S250 |  | ME42S2130 |  |  | 1 5/8 | 5/8
L5FGI4,4,3,2SS |  | 4,4,3,2 | 13Dr L5FG | 1 |  | Ice Cream | 22.8 | -23 | HG 2 Wire | 120 | 5.2 | 12.5 | 20.3 | 624 | 1500 | 2436 | ME14S250 |  | ME34S2110 |  |  | 1 3/8 | 5/8
|  | LPW PRODUCE ISLAND | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
LPW8 |  | 8' | LPW |  |  | Produce Table | 6.8 | 20 | Off Cycle | 120 | 0.4 |  |  | 48 | 0 | 0 |  |  | SORIT 12 |  |  | 1/2
LPW16 |  | 8'8' | LPW |  |  | Produce Table | 13.6 | 20 | Off Cycle | 120 | 0.8 |  |  | 96 | 0 | 0 |  |  | SORIT 12 |  |  | 5/8
LPW24 |  | 8'8'8' | LPW |  |  | Produce Table | 20.4 | 20 | Off Cycle | 120 | 1.2 |  |  | 144 | 0 | 0 |  |  | SORIT 12 |  |  | 7/8
LPW32 |  | 8'8'8'8' | LPW |  |  | Produce Table | 27.2 | 20 | Off Cycle | 120 | 1.6 |  |  | 192 | 0 | 0 |  |  | SORIT 12 |  |  | 7/8
L6DLR8 |  | 8' | L6DLR |  |  | Rear Load Dairy | 11.4 | 15 | Off Cycle | 120 | 0.6 | 3.4 |  | 72 | 408 | 0 |  |  | SORIT 12 |  |  | 5/8 | 1/2
L6DLR12 |  | 12' | L6DLR |  |  | Rear Load Dairy | 17.1 | 15 | Off Cycle | 120 | 0.9 | 6.3 |  | 108 | 756 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
L6DLR8'8 |  | 8'8' | 16' L6DLR |  |  | Rear Load Dairy | 22.8 | 15 | Off Cycle | 120 | 1.2 | 6.8 |  | 144 | 816 | 0 |  |  | SORIT 12 |  |  | 7/8 | 1/2
L6DLR8'12 |  | 8'12' | 20' L6DLR |  |  | Rear Load Dairy | 28.5 | 15 | Off Cycle | 120 | 1.5 | 9.7 |  | 180 | 1164 | 0 |  |  | SORIT 12 |  |  | 1 1/8 | 1/2
L6DLR8'8'8 |  | 8'8'8' | 24' L6DLR |  |  | Rear Load Dairy | 34.2 | 15 | Off Cycle | 120 | 1.8 | 10.2 |  | 216 | 1224 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
L6DLR12'12 |  | 12'12' | 24' L6DLR |  |  | Rear Load Dairy | 34.2 | 15 | Off Cycle | 120 | 1.8 | 12.6 |  | 216 | 1512 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 1/2
L6DLR8'8'12 |  | 8'8'12' | 28' L6DLR |  |  | Rear Load Dairy | 39.9 | 15 | Off Cycle | 120 | 2.1 | 13.1 |  | 252 | 1572 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
L6DLR8'8'8'8 |  | 8'8'8'8' | 32' L6DLR |  |  | Rear Load Dairy | 45.6 | 15 | Off Cycle | 120 | 2.4 | 13.6 |  | 288 | 1632 | 0 |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
L6DLR8'12'12 |  | 8'12'12' | 32' L6DLR |  |  | Rear Load Dairy | 45.6 | 15 | Off Cycle | 120 | 2.4 | 16 |  | 288 | 1920 | 0 |  |  | SORIT 15 |  |  | 1 3/8 | 5/8
L6DLR8'8'8'12 |  | 8'8'8'12' | 36' L6DLR |  |  | Rear Load Dairy | 51.3 | 15 | Off Cycle | 120 | 2.7 | 16.5 |  | 324 | 1980 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLR12'12'12 |  | 12'12'12' | 36' L6DLR |  |  | Rear Load Dairy | 51.3 | 15 | Off Cycle | 120 | 2.7 | 18.9 |  | 324 | 2268 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLR8'8'8'8'8 |  | 8'8'8'8'8' | 40' L6DLR |  |  | Rear Load Dairy | 57 | 15 | Off Cycle | 120 | 3 | 17 |  | 360 | 2040 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLR8'8'12'12 |  | 8'8'12'12' | 40' L6DLR |  |  | Rear Load Dairy | 57 | 15 | Off Cycle | 120 | 3 | 19.4 |  | 360 | 2328 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLR8'8'8'8'12 |  | 8'8'8'8'12' | 44' L6DLR |  |  | Rear Load Dairy | 62.7 | 15 | Off Cycle | 120 | 3.3 | 19.9 |  | 396 | 2388 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLR8'12'12'12 |  | 8'12'12'12' | 44' L6DLR |  |  | Rear Load Dairy | 62.7 | 15 | Off Cycle | 120 | 3.3 | 22.3 |  | 396 | 2676 | 0 |  |  | SORIT 20 |  |  | 1 3/8 | 5/8
L6DLR8'8'8'12'12 |  | 8'8'8'12'12' | 48' L6DLR |  |  | Rear Load Dairy | 68.4 | 15 | Off Cycle | 120 | 3.6 | 22.8 |  | 432 | 2736 | 0 | [5 empty] | 1 5/8 | 5/8
L6DLR12'12'12'12 |  | 12'12'12'12' | 48' L6DLR |  |  | Rear Load Dairy | 68.4 | 15 | Off Cycle | 120 | 3.6 | 25.2 |  | 432 | 3024 | 0 | [5 empty] | 1 5/8 | 5/8
[14 empty] | 0 | 0 | 0
|  | L5FG ICE CREAM W/EPR | [15 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
L5FGI2 |  | 2 | L5FG | 1 |  | Ice Cream | 3.5 | -23 | HG 2 Wire | 120 | 0.9 | 2.2 | 3.2 | 108 | 264 | 384 | ME14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
L5FGI3 |  | 3 | L5FG | 1 |  | Ice Cream | 5.3 | -23 | HG 2 Wire | 120 | 1.3 | 2.9 | 4.7 | 156 | 348 | 564 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L5FGI4 |  | 4 | L5FG | 1 |  | Ice Cream | 7 | -23 | HG 2 Wire | 120 | 1.5 | 3.7 | 6.2 | 180 | 444 | 744 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L5FGI5 |  | 5 | L5FG | 1 |  | Ice Cream | 8.8 | -23 | HG 2 Wire | 120 | 2 | 4.3 | 7.8 | 240 | 516 | 936 | ME14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
L5FGI3,3 |  | 3,3 | 6Dr L5FG | 1 |  | Ice Cream | 10.6 | -23 | HG 2 Wire | 120 | 2.6 | 5.8 | 9.4 | 312 | 696 | 1128 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FGI4,3 |  | 4,3 | 7Dr L5FG | 1 |  | Ice Cream | 12.3 | -23 | HG 2 Wire | 120 | 2.8 | 6.6 | 10.9 | 336 | 792 | 1308 | ME14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
L5FGI4,4 |  | 4,4 | 8Dr L5FG | 1 |  | Ice Cream | 14 | -23 | HG 2 Wire | 120 | 3 | 7.4 | 12.4 | 360 | 888 | 1488 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L5FGI5,3 |  | 5,3 | 8Dr L5FG | 1 |  | Ice Cream | 14.1 | -23 | HG 2 Wire | 120 | 3.3 | 7.2 | 12.5 | 396 | 864 | 1500 | ME14S250 |  | SORIT 15 |  |  | 1 1/8 | 5/8
L5FGI5,4 |  | 5,4 | 9Dr L5FG | 1 |  | Ice Cream | 15.8 | -23 | HG 2 Wire | 120 | 3.5 | 8 | 14 | 420 | 960 | 1680 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FGI3,3,3 |  | 3,3,3 | 9Dr L5FG | 1 |  | Ice Cream | 15.9 | -23 | HG 2 Wire | 120 | 3.9 | 8.7 | 14.1 | 468 | 1044 | 1692 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FGI5,5 |  | 5,5 | 10Dr L5FG | 1 |  | Ice Cream | 17.6 | -23 | HG 2 Wire | 120 | 4 | 8.6 | 15.6 | 480 | 1032 | 1872 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FGI4,3,3 |  | 4,3,3 | 10Dr L5FG | 1 |  | Ice Cream | 17.6 | -23 | HG 2 Wire | 120 | 4.1 | 9.5 | 15.6 | 492 | 1140 | 1872 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FGI5,3,3 |  | 5,3,3 | 11Dr L5FG | 1 |  | Ice Cream | 19.4 | -23 | HG 2 Wire | 120 | 4.6 | 10.1 | 17.2 | 552 | 1212 | 2064 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FGI4,4,3 |  | 4,4,3 | 11Dr L5FG | 1 |  | Ice Cream | 19.3 | -23 | HG 2 Wire | 120 | 4.3 | 10.3 | 17.1 | 516 | 1236 | 2052 | ME14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
L5FGI4,4,4 |  | 4,4,4 | 12Dr L5FG | 1 |  | Ice Cream | 21 | -23 | HG 2 Wire | 120 | 4.5 | 11.1 | 18.6 | 540 | 1332 | 2232 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L5FGI5,4,3 |  | 5,4,3 | 12Dr L5FG | 1 |  | Ice Cream | 21.1 | -23 | HG 2 Wire | 120 | 4.8 | 10.9 | 18.7 | 576 | 1308 | 2244 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L5FGI5,4,4 |  | 5,4,4 | 13Dr L5FG | 1 |  | Ice Cream | 22.8 | -23 | HG 2 Wire | 120 | 5 | 11.7 | 20.2 | 600 | 1404 | 2424 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L5FGI5,5,3 |  | 5,5,3 | 13Dr L5FG | 1 |  | Ice Cream | 22.9 | -23 | HG 2 Wire | 120 | 5.3 | 11.5 | 20.3 | 636 | 1380 | 2436 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
L5FGI5,5,4 |  | 5,5,4 | 14Dr L5FG | 1 |  | Ice Cream | 24.6 | -23 | HG 2 Wire | 120 | 5.5 | 12.3 | 21.8 | 660 | 1476 | 2616 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L5FGI4,4,3,3 |  | 4,4,3,3 | 14Dr L5FG | 1 |  | Ice Cream | 24.6 | -23 | HG 2 Wire | 120 | 5.6 | 13.2 | 21.8 | 672 | 1584 | 2616 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L5FGI5,5,5 |  | 5,5,5 | 15Dr L5FG | 1 |  | Ice Cream | 26.4 | -23 | HG 2 Wire | 120 | 6 | 12.9 | 23.4 | 720 | 1548 | 2808 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L5FGI4,4,4,3 |  | 4,4,4,3 | 15Dr L5FG | 1 |  | Ice Cream | 26.3 | -23 | HG 2 Wire | 120 | 5.8 | 14 | 23.3 | 696 | 1680 | 2796 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L5FGI5,5,3,3 |  | 5,5,3,3 | 16Dr L5FG | 1 |  | Ice Cream | 28.2 | -23 | HG 2 Wire | 120 | 6.6 | 14.4 | 25 | 792 | 1728 | 3000 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L5FGI4,4,4,4 |  | 4,4,4,4 | 16Dr L5FG | 1 |  | Ice Cream | 28 | -23 | HG 2 Wire | 120 | 6 | 14.8 | 24.8 | 720 | 1776 | 2976 | ME14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
L5FGI4,4,3,2 |  | 4,4,3,2 | 13Dr L5FG | 1 |  | Ice Cream | 22.8 | -23 | HG 2 Wire | 120 | 5.2 | 12.5 | 20.3 | 624 | 1500 | 2436 | ME14S250 |  | SORIT 20 |  |  | 1 3/8 | 5/8
|  | 05DM MD DAIRY/ Cut Produce | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4O5DM |  | 4' | 4' O5DM-E | 1 |  | MD Dairy | 5.724 | 26 | Off Cycle | 120 | 0.47 | 0.23 |  | 56.4 | 27.6 | 0 |  |  | SORIT 12 |  |  | 1/2
6O5DM |  | 6' | 6' O5DM-E | 1 |  | MD Dairy | 8.586 | 26 | Off Cycle | 120 | 0.47 | 0.37 |  | 56.4 | 44.4 | 0 |  |  | SORIT 12 |  |  | 5/8
8O5DM |  | 8' | 8' O5DM-E | 1 |  | MD Dairy | 11.448 | 26 | Off Cycle | 120 | 0.7 | 0.47 |  | 84 | 56.4 | 0 |  |  | SORIT 12 |  |  | 1/2
12O5DM |  | 12' | 12' O5DM-E | 1 |  | MD Dairy | 17.172 | 26 | Off Cycle | 120 | 0.93 | 0.7 |  | 111.6 | 84 | 0 |  |  | SORIT 12 |  |  | 5/8
8'8O5DM |  | 8'8' | 16' O5DM-E | 1 |  | MD Dairy | 22.896 | 26 | Off Cycle | 120 | 1.4 | 0.94 |  | 168 | 112.8 | 0 |  |  | SORIT 12 |  |  | 5/8
8'12O5DM |  | 8'12' | 20' O5DM-E | 1 |  | MD Dairy | 28.62 | 26 | Off Cycle | 120 | 1.63 | 1.17 |  | 195.6 | 140.4 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'8O5DM |  | 8'8'8' | 24' O5DM-E | 1 |  | MD Dairy | 34.344 | 26 | Off Cycle | 120 | 2.1 | 1.41 |  | 252 | 169.2 | 0 |  |  | SORIT 12 |  |  | 7/8
12'12O5DM |  | 12'12' | 24' O5DM-E | 1 |  | MD Dairy | 34.344 | 26 | Off Cycle | 120 | 1.86 | 1.4 |  | 223.2 | 168 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'12O5DM |  | 8'8'12' | 28' O5DM-E | 1 |  | MD Dairy | 40.068 | 26 | Off Cycle | 120 | 2.33 | 1.64 |  | 279.6 | 196.8 | 0 |  |  | SORIT 15 |  |  | 7/8
8'8'8'8O5DM |  | 8'8'8'8' | 32' O5DM-E | 1 |  | MD Dairy | 45.792 | 26 | Off Cycle | 120 | 2.8 | 1.88 |  | 336 | 225.6 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'12'12O5DM |  | 8'12'12' | 32' O5DM-E | 1 |  | MD Dairy | 45.792 | 26 | Off Cycle | 120 | 2.56 | 1.87 |  | 307.2 | 224.4 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8'12O5DM |  | 8'8'8'12' | 36' O5DM-E | 1 |  | MD Dairy | 51.516 | 26 | Off Cycle | 120 | 3.03 | 2.11 |  | 363.6 | 253.2 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12O5DM |  | 12'12'12' | 36' O5DM-E | 1 |  | MD Dairy | 51.516 | 26 | Off Cycle | 120 | 2.79 | 2.1 |  | 334.8 | 252 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'8O5DM |  | 8'8'8'8'8' | 40' O5DM-E | 1 |  | MD Dairy | 57.24 | 26 | Off Cycle | 120 | 3.5 | 2.35 |  | 420 | 282 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12O5DM |  | 8'8'12'12' | 40' O5DM-E | 1 |  | MD Dairy | 57.24 | 26 | Off Cycle | 120 | 3.26 | 2.34 |  | 391.2 | 280.8 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12O5DM |  | 8'8'8'8'12' | 44' O5DM-E | 1 |  | MD Dairy | 62.964 | 26 | Off Cycle | 120 | 3.73 | 2.58 |  | 447.6 | 309.6 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12O5DM |  | 8'12'12'12' | 44' O5DM-E | 1 |  | MD Dairy | 62.964 | 26 | Off Cycle | 120 | 3.49 | 2.57 |  | 418.8 | 308.4 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12O5DM |  | 8'8'8'12'12' | 48' O5DM-E | 1 |  | MD Dairy | 68.688 | 26 | Off Cycle | 120 | 3.96 | 2.81 |  | 475.2 | 337.2 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12O5DM |  | 12'12'12'12' | 48' O5DM-E | 1 |  | MD Dairy | 68.688 | 26 | Off Cycle | 120 | 3.72 | 2.8 |  | 446.4 | 336 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | 05DM MD Deli Meat | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4O5DMDM |  | 4' | 4' O5DM-E | 1 |  | MD Deli Meat | 6.28 | 22 | Off Cycle | 120 | 0.47 | 0.23 |  | 56.4 | 27.6 | 0 |  |  | SORIT 12 |  |  | 1/2
6O5DMDM |  | 6' | 6' O5DM-E | 1 |  | MD Deli Meat | 9.42 | 22 | Off Cycle | 120 | 0.47 | 0.37 |  | 56.4 | 44.4 | 0 |  |  | SORIT 12 |  |  | 5/8
8O5DMDM |  | 8' | 8' O5DM-E | 1 |  | MD Deli Meat | 12.56 | 22 | Off Cycle | 120 | 0.7 | 0.47 |  | 84 | 56.4 | 0 |  |  | SORIT 12 |  |  | 1/2
12O5DMDM |  | 12' | 12' O5DM-E | 1 |  | MD Deli Meat | 18.84 | 22 | Off Cycle | 120 | 0.93 | 0.7 |  | 111.6 | 84 | 0 |  |  | SORIT 12 |  |  | 5/8
8'8O5DMDM |  | 8'8' | 16' O5DM-E | 1 |  | MD Deli Meat | 25.12 | 22 | Off Cycle | 120 | 1.4 | 0.94 |  | 168 | 112.8 | 0 |  |  | SORIT 12 |  |  | 5/8
8'12O5DMDM |  | 8'12' | 20' O5DM-E | 1 |  | MD Deli Meat | 31.4 | 22 | Off Cycle | 120 | 1.63 | 1.17 |  | 195.6 | 140.4 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'8O5DMDM |  | 8'8'8' | 24' O5DM-E | 1 |  | MD Deli Meat | 37.68 | 22 | Off Cycle | 120 | 2.1 | 1.41 |  | 252 | 169.2 | 0 |  |  | SORIT 12 |  |  | 7/8
12'12O5DMDM |  | 12'12' | 24' O5DM-E | 1 |  | MD Deli Meat | 37.68 | 22 | Off Cycle | 120 | 1.86 | 1.4 |  | 223.2 | 168 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'12O5DMDM |  | 8'8'12' | 28' O5DM-E | 1 |  | MD Deli Meat | 43.96 | 22 | Off Cycle | 120 | 2.33 | 1.64 |  | 279.6 | 196.8 | 0 |  |  | SORIT 15 |  |  | 7/8
8'8'8'8O5DMDM |  | 8'8'8'8' | 32' O5DM-E | 1 |  | MD Deli Meat | 50.24 | 22 | Off Cycle | 120 | 2.8 | 1.88 |  | 336 | 225.6 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'12'12O5DMDM |  | 8'12'12' | 32' O5DM-E | 1 |  | MD Deli Meat | 50.24 | 22 | Off Cycle | 120 | 2.56 | 1.87 |  | 307.2 | 224.4 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8'12O5DMDM |  | 8'8'8'12' | 36' O5DM-E | 1 |  | MD Deli Meat | 56.52 | 22 | Off Cycle | 120 | 3.03 | 2.11 |  | 363.6 | 253.2 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12O5DMDM |  | 12'12'12' | 36' O5DM-E | 1 |  | MD Deli Meat | 56.52 | 22 | Off Cycle | 120 | 2.79 | 2.1 |  | 334.8 | 252 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'8O5DMDM |  | 8'8'8'8'8' | 40' O5DM-E | 1 |  | MD Deli Meat | 62.8 | 22 | Off Cycle | 120 | 3.5 | 2.35 |  | 420 | 282 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12O5DMDM |  | 8'8'12'12' | 40' O5DM-E | 1 |  | MD Deli Meat | 62.8 | 22 | Off Cycle | 120 | 3.26 | 2.34 |  | 391.2 | 280.8 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12O5DMDM |  | 8'8'8'8'12' | 44' O5DM-E | 1 |  | MD Deli Meat | 69.08 | 22 | Off Cycle | 120 | 3.73 | 2.58 |  | 447.6 | 309.6 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12O5DMDM |  | 8'12'12'12' | 44' O5DM-E | 1 |  | MD Deli Meat | 69.08 | 22 | Off Cycle | 120 | 3.49 | 2.57 |  | 418.8 | 308.4 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12O5DMDM |  | 8'8'8'12'12' | 48' O5DM-E | 1 |  | MD Deli Meat | 75.36 | 22 | Off Cycle | 120 | 3.96 | 2.81 |  | 475.2 | 337.2 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12O5DMDM |  | 12'12'12'12' | 48' O5DM-E | 1 |  | MD Deli Meat | 75.36 | 22 | Off Cycle | 120 | 3.72 | 2.8 |  | 446.4 | 336 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | ORS5DM MD DAIRY/ DELI | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
[14 empty] | 0 | 0 | 0 |  |  | SORIT 12
8ORS5DM |  | 8' | 8' ORS5DM | 1 |  | MD Dairy | 1.756 | 32 | Off Cycle | 120 | 0.46 | 0.39 | 1.49 | 55.2 | 46.8 | 178.8 |  |  | SORIT 12
12ORS5DM |  | 12' | 12' ORS5DM | 1 |  | MD Dairy | 2.634 | 32 | Off Cycle | 120 | 0.61 | 0.58 | 1.94 | 73.2 | 69.6 | 232.8 |  |  | SORIT 12
8'8ORS5DM |  | 8'8' | 16' ORS5DM | 1 |  | MD Dairy | 3.512 | 32 | Off Cycle | 120 | 0.92 | 0.78 | 2.98 | 110.4 | 93.6 | 357.6 |  |  | SORIT 12
8'12ORS5DM |  | 8'12' | 20' ORS5DM | 1 |  | MD Dairy | 4.39 | 32 | Off Cycle | 120 | 1.07 | 0.97 | 3.43 | 128.4 | 116.4 | 411.6 |  |  | SORIT 12
8'8'8ORS5DM |  | 8'8'8' | 24' ORS5DM | 1 |  | MD Dairy | 5.268 | 32 | Off Cycle | 120 | 1.38 | 1.17 | 4.47 | 165.6 | 140.4 | 536.4 |  |  | SORIT 12
12'12ORS5DM |  | 12'12' | 24' ORS5DM | 1 |  | MD Dairy | 5.268 | 32 | Off Cycle | 120 | 1.22 | 1.16 | 3.88 | 146.4 | 139.2 | 465.6 |  |  | SORIT 12
8'8'12ORS5DM |  | 8'8'12' | 28' ORS5DM | 1 |  | MD Dairy | 6.146 | 32 | Off Cycle | 120 | 1.53 | 1.36 | 4.92 | 183.6 | 163.2 | 590.4 |  |  | SORIT 12
8'8'8'8ORS5DM |  | 8'8'8'8' | 32' ORS5DM | 1 |  | MD Dairy | 7.024 | 32 | Off Cycle | 120 | 1.84 | 1.56 | 5.96 | 220.8 | 187.2 | 715.2 |  |  | SORIT 12
8'12'12ORS5DM |  | 8'12'12' | 32' ORS5DM | 1 |  | MD Dairy | 7.024 | 32 | Off Cycle | 120 | 1.68 | 1.55 | 5.37 | 201.6 | 186 | 644.4 |  |  | SORIT 12
8'8'8'12ORS5DM |  | 8'8'8'12' | 36' ORS5DM | 1 |  | MD Dairy | 7.902 | 32 | Off Cycle | 120 | 1.99 | 1.75 | 6.41 | 238.8 | 210 | 769.2 |  |  | SORIT 12
12'12'12ORS5DM |  | 12'12'12' | 36' ORS5DM | 1 |  | MD Dairy | 7.902 | 32 | Off Cycle | 120 | 1.83 | 1.74 | 5.82 | 219.6 | 208.8 | 698.4 |  |  | SORIT 12
8'8'8'8'8ORS5DM |  | 8'8'8'8'8' | 40' ORS5DM | 1 |  | MD Dairy | 8.78 | 32 | Off Cycle | 120 | 2.3 | 1.95 | 7.45 | 276 | 234 | 894 |  |  | SORIT 12
8'8'12'12ORS5DM |  | 8'8'12'12' | 40' ORS5DM | 1 |  | MD Dairy | 8.78 | 32 | Off Cycle | 120 | 2.14 | 1.94 | 6.86 | 256.8 | 232.8 | 823.2 |  |  | SORIT 12
8'8'8'8'12ORS5DM |  | 8'8'8'8'12' | 44' ORS5DM | 1 |  | MD Dairy | 9.658 | 32 | Off Cycle | 120 | 2.45 | 2.14 | 7.9 | 294 | 256.8 | 948 |  |  | SORIT 12
8'12'12'12ORS5DM |  | 8'12'12'12' | 44' ORS5DM | 1 |  | MD Dairy | 9.658 | 32 | Off Cycle | 120 | 2.29 | 2.13 | 7.31 | 274.8 | 255.6 | 877.2 |  |  | SORIT 12
8'8'8'12'12ORS5DM |  | 8'8'8'12'12' | 48' ORS5DM | 1 |  | MD Dairy | 10.536 | 32 | Off Cycle | 120 | 2.6 | 2.33 | 8.35 | 312 | 279.6 | 1002 |  |  | SORIT 12
12'12'12'12ORS5DM |  | 12'12'12'12' | 48' ORS5DM | 1 |  | MD Dairy | 10.536 | 32 | Off Cycle | 120 | 2.44 | 2.32 | 7.76 | 292.8 | 278.4 | 931.2 |  |  | SORIT 12
12'12'12'12'12ORS5DM |  | 5) 12'S | 60 ORS5DM | 1 |  | MD Dairy | 15.804 | 32 | Off Cycle | 120 | 3.66 | 3.48 | 11.64 | 439.2 | 417.6 | 1396.8
|  | ORS5DM MD BEVERAGE | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
[14 empty] | 0 | 0 | 0 |  |  | SORIT 12
8ORS5DMB |  | 8' | 8' ORS5DM | 1 |  | MD Beverage | 1.66 | 34 | Off Cycle | 120 | 0.46 | 0.39 | 1.49 | 55.2 | 46.8 | 178.8 |  |  | SORIT 12
12ORS5DMB |  | 12' | 12' ORS5DM | 1 |  | MD Beverage | 2.49 | 34 | Off Cycle | 120 | 0.61 | 0.58 | 1.94 | 73.2 | 69.6 | 232.8 |  |  | SORIT 12
8'8ORS5DMB |  | 8'8' | 16' ORS5DM | 1 |  | MD Beverage | 3.32 | 34 | Off Cycle | 120 | 0.92 | 0.78 | 2.98 | 110.4 | 93.6 | 357.6 |  |  | SORIT 12
8'12ORS5DMB |  | 8'12' | 20' ORS5DM | 1 |  | MD Beverage | 4.15 | 34 | Off Cycle | 120 | 1.07 | 0.97 | 3.43 | 128.4 | 116.4 | 411.6 |  |  | SORIT 12
8'8'8ORS5DMB |  | 8'8'8' | 24' ORS5DM | 1 |  | MD Beverage | 4.98 | 34 | Off Cycle | 120 | 1.38 | 1.17 | 4.47 | 165.6 | 140.4 | 536.4 |  |  | SORIT 12
12'12ORS5DMB |  | 12'12' | 24' ORS5DM | 1 |  | MD Beverage | 4.98 | 34 | Off Cycle | 120 | 1.22 | 1.16 | 3.88 | 146.4 | 139.2 | 465.6 |  |  | SORIT 12
8'8'12ORS5DMB |  | 8'8'12' | 28' ORS5DM | 1 |  | MD Beverage | 5.81 | 34 | Off Cycle | 120 | 1.53 | 1.36 | 4.92 | 183.6 | 163.2 | 590.4 |  |  | SORIT 12
8'8'8'8ORS5DMB |  | 8'8'8'8' | 32' ORS5DM | 1 |  | MD Beverage | 6.64 | 34 | Off Cycle | 120 | 1.84 | 1.56 | 5.96 | 220.8 | 187.2 | 715.2 |  |  | SORIT 12
8'12'12ORS5DMB |  | 8'12'12' | 32' ORS5DM | 1 |  | MD Beverage | 6.64 | 34 | Off Cycle | 120 | 1.68 | 1.55 | 5.37 | 201.6 | 186 | 644.4 |  |  | SORIT 12
8'8'8'12ORS5DMB |  | 8'8'8'12' | 36' ORS5DM | 1 |  | MD Beverage | 7.47 | 34 | Off Cycle | 120 | 1.99 | 1.75 | 6.41 | 238.8 | 210 | 769.2 |  |  | SORIT 12
12'12'12ORS5DMB |  | 12'12'12' | 36' ORS5DM | 1 |  | MD Beverage | 7.47 | 34 | Off Cycle | 120 | 1.83 | 1.74 | 5.82 | 219.6 | 208.8 | 698.4 |  |  | SORIT 12
8'8'8'8'8ORS5DMB |  | 8'8'8'8'8' | 40' ORS5DM | 1 |  | MD Beverage | 8.3 | 34 | Off Cycle | 120 | 2.3 | 1.95 | 7.45 | 276 | 234 | 894 |  |  | SORIT 12
8'8'12'12ORS5DMB |  | 8'8'12'12' | 40' ORS5DM | 1 |  | MD Beverage | 8.3 | 34 | Off Cycle | 120 | 2.14 | 1.94 | 6.86 | 256.8 | 232.8 | 823.2 |  |  | SORIT 12
8'8'8'8'12ORS5DMB |  | 8'8'8'8'12' | 44' ORS5DM | 1 |  | MD Beverage | 9.13 | 34 | Off Cycle | 120 | 2.45 | 2.14 | 7.9 | 294 | 256.8 | 948 |  |  | SORIT 12
8'12'12'12ORS5DMB |  | 8'12'12'12' | 44' ORS5DM | 1 |  | MD Beverage | 9.13 | 34 | Off Cycle | 120 | 2.29 | 2.13 | 7.31 | 274.8 | 255.6 | 877.2 |  |  | SORIT 12
8'8'8'12'12ORS5DMB |  | 8'8'8'12'12' | 48' ORS5DM | 1 |  | MD Beverage | 9.96 | 34 | Off Cycle | 120 | 2.6 | 2.33 | 8.35 | 312 | 279.6 | 1002 |  |  | SORIT 12
12'12'12'12ORS5DMB |  | 12'12'12'12' | 48' ORS5DM | 1 |  | MD Beverage | 9.96 | 34 | Off Cycle | 120 | 2.44 | 2.32 | 7.76 | 292.8 | 278.4 | 931.2 |  |  | SORIT 12
12'12'12'12'12ORS5DM |  | 5) 12'S | 60 ORS5DM | 1 |  | MD Beverage | 14.94 | 34 | Off Cycle | 120 | 3.66 | 3.48 | 11.64 | 439.2 | 417.6 | 1396.8 |  |  | SORIT 12
|  | 05DM-EB MD BEVERAGE | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4O5DMB |  | 4' | 4' O5DM-E | 1 |  | MD Beer | 5.8 | 26 | Off Cycle | 120 | 0.47 | 0.23 |  | 56.4 | 27.6 | 0 |  |  | SORIT 12 |  |  | 1/2
6O5DMB |  | 6' | 6' O5DM-E | 1 |  | MD Beer | 8.7 | 26 | Off Cycle | 120 | 0.47 | 0.37 |  | 56.4 | 44.4 | 0 |  |  | SORIT 12 |  |  | 5/8
8O5DMB |  | 8' | 8' O5DM-E | 1 |  | MD Beer | 11.6 | 26 | Off Cycle | 120 | 0.7 | 0.47 |  | 84 | 56.4 | 0 |  |  | SORIT 12 |  |  | 1/2
12O5DMB |  | 12' | 12' O5DM-E | 1 |  | MD Beer | 17.4 | 26 | Off Cycle | 120 | 0.93 | 0.7 |  | 111.6 | 84 | 0 |  |  | SORIT 12 |  |  | 5/8
8'8O5DMB |  | 8'8' | 16' O5DM-E | 1 |  | MD Beer | 23.2 | 26 | Off Cycle | 120 | 1.4 | 0.94 |  | 168 | 112.8 | 0 |  |  | SORIT 12 |  |  | 5/8
8'12O5DMB |  | 8'12' | 20' O5DM-E | 1 |  | MD Beer | 29 | 26 | Off Cycle | 120 | 1.63 | 1.17 |  | 195.6 | 140.4 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'8O5DMB |  | 8'8'8' | 24' O5DM-E | 1 |  | MD Beer | 34.8 | 26 | Off Cycle | 120 | 2.1 | 1.41 |  | 252 | 169.2 | 0 |  |  | SORIT 12 |  |  | 7/8
12'12O5DMB |  | 12'12' | 24' O5DM-E | 1 |  | MD Beer | 34.8 | 26 | Off Cycle | 120 | 1.86 | 1.4 |  | 223.2 | 168 | 0 |  |  | SORIT 12 |  |  | 7/8
8'8'12O5DMB |  | 8'8'12' | 28' O5DM-E | 1 |  | MD Beer | 40.6 | 26 | Off Cycle | 120 | 2.33 | 1.64 |  | 279.6 | 196.8 | 0 |  |  | SORIT 15 |  |  | 7/8
8'8'8'805DMB |  | 8'8'8'8' | 32' O5DM-E | 1 |  | MD Beer | 46.4 | 26 | Off Cycle | 120 | 2.8 | 1.88 |  | 336 | 225.6 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'12'1205DMB |  | 8'12'12' | 32' O5DM-E | 1 |  | MD Beer | 46.4 | 26 | Off Cycle | 120 | 2.56 | 1.87 |  | 307.2 | 224.4 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8'12O5DMB |  | 8'8'8'12' | 36' O5DM-E | 1 |  | MD Beer | 52.2 | 26 | Off Cycle | 120 | 3.03 | 2.11 |  | 363.6 | 253.2 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
12'12'12O5DMB |  | 12'12'12' | 36' O5DM-E | 1 |  | MD Beer | 52.2 | 26 | Off Cycle | 120 | 2.79 | 2.1 |  | 334.8 | 252 | 0 |  |  | SORIT 15 |  |  | 1 1/8 | 5/8
8'8'8'8'8O5DMB |  | 8'8'8'8'8' | 40' O5DM-E | 1 |  | MD Beer | 58 | 26 | Off Cycle | 120 | 3.5 | 2.35 |  | 420 | 282 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'12'12O5DMB |  | 8'8'12'12' | 40' O5DM-E | 1 |  | MD Beer | 58 | 26 | Off Cycle | 120 | 3.26 | 2.34 |  | 391.2 | 280.8 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'8'12O5DMB |  | 8'8'8'8'12' | 44' O5DM-E | 1 |  | MD Beer | 63.8 | 26 | Off Cycle | 120 | 3.73 | 2.58 |  | 447.6 | 309.6 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'12'12'12O5DMB |  | 8'12'12'12' | 44' O5DM-E | 1 |  | MD Beer | 63.8 | 26 | Off Cycle | 120 | 3.49 | 2.57 |  | 418.8 | 308.4 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
8'8'8'12'12O5DMB |  | 8'8'8'12'12' | 48' O5DM-E | 1 |  | MD Beer | 69.6 | 26 | Off Cycle | 120 | 3.96 | 2.81 |  | 475.2 | 337.2 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
12'12'12'12O5DMB |  | 12'12'12'12' | 48' O5DM-E | 1 |  | MD Beer | 69.6 | 26 | Off Cycle | 120 | 3.72 | 2.8 |  | 446.4 | 336 | 0 |  |  | SORIT 20 |  |  | 1 1/8 | 5/8
|  | O3UM-E MD FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4O3UM |  | 4' | 4' O3UM-E | 1 |  | 3D Fresh Meat | 4.12 | 22 | Off Cycle | 120 | 0.15 | 0.93 | 0.28 | 18 | 111.6 | 33.6 |  |  | SORIT 12 |  |  | 1/2
6O3UM |  | 6' | 6' O3UM-E | 1 |  | 3D Fresh Meat | 6.18 | 22 | Off Cycle | 120 | 0.15 | 1.47 | 0.4 | 18 | 176.4 | 48 |  |  | SORIT 12 |  |  | 1/2
8O3UM |  | 8' | 8' O3UM-E | 1 |  | 3D Fresh Meat | 8.24 | 22 | Off Cycle | 120 | 0.23 | 1.87 | 0.5 | 27.6 | 224.4 | 60 |  |  | SORIT 12 |  |  | 7/8
12O3UM |  | 12' | 12' O3UM-E | 1 |  | 3D Fresh Meat | 12.36 | 22 | Off Cycle | 120 | 0.31 | 2.8 | 0.76 | 37.2 | 336 | 91.2 |  |  | SORIT 12 |  |  | 7/8
8'8O3UM |  | 8'8' | 16' O3UM-E | 1 |  | 3D Fresh Meat | 16.48 | 22 | Off Cycle | 120 | 0.46 | 3.74 | 1 | 55.2 | 448.8 | 120 |  |  | SORIT 12 |  |  | 1 1/8
8'12O3UM |  | 8'12' | 20' O3UM-E | 1 |  | 3D Fresh Meat | 20.6 | 22 | Off Cycle | 120 | 0.54 | 4.67 | 1.26 | 64.8 | 560.4 | 151.2 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8O3UM |  | 8'8'8' | 24' O3UM-E | 1 |  | 3D Fresh Meat | 24.72 | 22 | Off Cycle | 120 | 0.69 | 5.61 | 1.5 | 82.8 | 673.2 | 180 |  |  | SORIT 15 |  |  | 1 3/8
12'12O3UM |  | 12'12' | 24' O3UM-E | 1 |  | 3D Fresh Meat | 24.72 | 22 | Off Cycle | 120 | 0.62 | 5.6 | 1.52 | 74.4 | 672 | 182.4 |  |  | SORIT 15 |  |  | 1 3/8
8'8'12O3UM |  | 8'8'12' | 28' O3UM-E | 1 |  | 3D Fresh Meat | 28.84 | 22 | Off Cycle | 120 | 0.77 | 6.54 | 1.76 | 92.4 | 784.8 | 211.2 |  |  | SORIT 20 |  |  | 1 3/8
8'8'8'8O3UM |  | 8'8'8'8' | 32' O3UM-E | 1 |  | 3D Fresh Meat | 32.96 | 22 | Off Cycle | 120 | 0.92 | 7.48 | 2 | 110.4 | 897.6 | 240 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12O3UM |  | 8'12'12' | 32' O3UM-E | 1 |  | 3D Fresh Meat | 32.96 | 22 | Off Cycle | 120 | 0.85 | 7.47 | 2.02 | 102 | 896.4 | 242.4 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12O3UM |  | 8'8'8'12' | 36' O3UM-E | 1 |  | 3D Fresh Meat | 37.08 | 22 | Off Cycle | 120 | 1 | 8.41 | 2.26 | 120 | 1009.2 | 271.2 |  |  | SORIT 20 |  |  | 1 5/8
12'12'12O3UM |  | 12'12'12' | 36' O3UM-E | 1 |  | 3D Fresh Meat | 37.08 | 22 | Off Cycle | 120 | 0.93 | 8.4 | 2.28 | 111.6 | 1008 | 273.6 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'8O3UM |  | 8'8'8'8'8' | 40' O3UM-E | 1 |  | 3D Fresh Meat | 41.2 | 22 | Off Cycle | 120 | 1.15 | 9.35 | 2.5 | 138 | 1122 | 300 |  |  | SORIT 20 |  |  | 1 5/8
8'8'12'12O3UM |  | 8'8'12'12' | 40' O3UM-E | 1 |  | 3D Fresh Meat | 41.2 | 22 | Off Cycle | 120 | 1.08 | 9.34 | 2.52 | 129.6 | 1120.8 | 302.4 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'12O3UM |  | 8'8'8'8'12' | 44' O3UM-E | 1 |  | 3D Fresh Meat | 45.32 | 22 | Off Cycle | 120 | 1.23 | 10.28 | 2.76 | 147.6 | 1233.6 | 331.2 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12'12O3UM |  | 8'12'12'12' | 44' O3UM-E | 1 |  | 3D Fresh Meat | 45.32 | 22 | Off Cycle | 120 | 1.16 | 10.27 | 2.78 | 139.2 | 1232.4 | 333.6 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12'12O3UM |  | 8'8'8'12'12' | 48' O3UM-E | 1 |  | 3D Fresh Meat | 49.44 | 22 | Off Cycle | 120 | 1.31 | 11.21 | 3.02 | 157.2 | 1345.2 | 362.4 |  |  | SORIT 20 |  |  | 2 1/8
12'12'12'12O3UM |  | 12'12'12'12' | 48' O3UM-E | 1 |  | 3D Fresh Meat | 49.44 | 22 | Off Cycle | 120 | 1.24 | 11.2 | 3.04 | 148.8 | 1344 | 364.8 |  |  | SORIT 20 |  |  | 2 1/8
|  | O4UM-E Deli | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4O4UM |  | 4' | 4' O4UM-E | 1 |  | 3D Fresh Meat | 5.472 | 22 | Off Cycle | 120 | 0.39 | 0.46 | 0.28 | 46.8 | 55.2 | 33.6 | [5 empty] | 1/2
6O4UM |  | 6' | 6' O4UM-E | 1 |  | 3D Fresh Meat | 8.208 | 22 | Off Cycle | 120 | 0.39 | 0.74 | 0.4 | 46.8 | 88.8 | 48 | [5 empty] | 1/2
8O4UM |  | 8' | 8' O4UM-E | 1 |  | 3D Fresh Meat | 10.944 | 22 | Off Cycle | 120 | 0.59 | 0.94 | 0.5 | 70.8 | 112.8 | 60 | [5 empty] | 7/8
12O4UM |  | 12' | 12' O4UM-E | 1 |  | 3D Fresh Meat | 16.416 | 22 | Off Cycle | 120 | 0.78 | 1.4 | 0.76 | 93.6 | 168 | 91.2 | [5 empty] | 7/8
8'8O4UM |  | 8'8' | 16' O4UM-E | 1 |  | 3D Fresh Meat | 21.888 | 22 | Off Cycle | 120 | 1.18 | 1.88 | 1 | 141.6 | 225.6 | 120 | [5 empty] | 1 1/8
8'12O4UM |  | 8'12' | 20' O4UM-E | 1 |  | 3D Fresh Meat | 27.36 | 22 | Off Cycle | 120 | 1.37 | 2.34 | 1.26 | 164.4 | 280.8 | 151.2 | [5 empty] | 1 1/8
8'8'8O4UM |  | 8'8'8' | 24' O4UM-E | 1 |  | 3D Fresh Meat | 32.832 | 22 | Off Cycle | 120 | 1.77 | 2.82 | 1.5 | 212.4 | 338.4 | 180 | [5 empty] | 1 3/8
12'12O4UM |  | 12'12' | 24' O4UM-E | 1 |  | 3D Fresh Meat | 32.832 | 22 | Off Cycle | 120 | 1.56 | 2.8 | 1.52 | 187.2 | 336 | 182.4 | [5 empty] | 1 3/8
8'8'12O4UM |  | 8'8'12' | 28' O4UM-E | 1 |  | 3D Fresh Meat | 38.304 | 22 | Off Cycle | 120 | 1.96 | 3.28 | 1.76 | 235.2 | 393.6 | 211.2 | [5 empty] | 1 3/8
8'8'8'8O4UM |  | 8'8'8'8' | 32' O4UM-E | 1 |  | 3D Fresh Meat | 43.776 | 22 | Off Cycle | 120 | 2.36 | 3.76 | 2 | 283.2 | 451.2 | 240 | [5 empty] | 1 5/8
8'12'12O4UM |  | 8'12'12' | 32' O4UM-E | 1 |  | 3D Fresh Meat | 43.776 | 22 | Off Cycle | 120 | 2.15 | 3.74 | 2.02 | 258 | 448.8 | 242.4 | [5 empty] | 1 5/8
8'8'8'12O4UM |  | 8'8'8'12' | 36' O4UM-E | 1 |  | 3D Fresh Meat | 49.248 | 22 | Off Cycle | 120 | 2.55 | 4.22 | 2.26 | 306 | 506.4 | 271.2 | [5 empty] | 1 5/8
12'12'12O4UM |  | 12'12'12' | 36' O4UM-E | 1 |  | 3D Fresh Meat | 49.248 | 22 | Off Cycle | 120 | 2.34 | 4.2 | 2.28 | 280.8 | 504 | 273.6 | [5 empty] | 1 5/8
8'8'8'8'8O4UM |  | 8'8'8'8'8' | 40' O4UM-E | 1 |  | 3D Fresh Meat | 54.72 | 22 | Off Cycle | 120 | 2.95 | 4.7 | 2.5 | 354 | 564 | 300 | [5 empty] | 1 5/8
8'8'12'12O4UM |  | 8'8'12'12' | 40' O4UM-E | 1 |  | 3D Fresh Meat | 54.72 | 22 | Off Cycle | 120 | 2.74 | 4.68 | 2.52 | 328.8 | 561.6 | 302.4 | [5 empty] | 1 5/8
8'8'8'8'12O4UM |  | 8'8'8'8'12' | 44' O4UM-E | 1 |  | 3D Fresh Meat | 60.192 | 22 | Off Cycle | 120 | 3.14 | 5.16 | 2.76 | 376.8 | 619.2 | 331.2 | [5 empty] | 1 5/8
8'12'12'12O4UM |  | 8'12'12'12' | 44' O4UM-E | 1 |  | 3D Fresh Meat | 60.192 | 22 | Off Cycle | 120 | 2.93 | 5.14 | 2.78 | 351.6 | 616.8 | 333.6 | [5 empty] | 1 5/8
8'8'8'12'12O4UM |  | 8'8'8'12'12' | 48' O4UM-E | 1 |  | 3D Fresh Meat | 65.664 | 22 | Off Cycle | 120 | 3.33 | 5.62 | 3.02 | 399.6 | 674.4 | 362.4 | [5 empty] | 2 1/8
12'12'12'12O4UM |  | 12'12'12'12' | 48' O4UM-E | 1 |  | 3D Fresh Meat | 65.664 | 22 | Off Cycle | 120 | 3.12 | 5.6 | 3.04 | 374.4 | 672 | 364.8 | [5 empty] | 2 1/8
|  | OM-E FRESH MEAT | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4OM |  | 4' | 4' OM-E | 1 |  | Fresh Meat | 1.92 | 22 | Off Cycle | 120 | 0.15 | 1.67 | 0.28 | 18 | 200.4 | 33.6 |  |  | SORIT 12 |  |  | 1/2
6OM |  | 6' | 6' OM-E | 1 |  | Fresh Meat | 2.88 | 22 | Off Cycle | 120 | 0.15 | 1.83 | 0.4 | 18 | 219.6 | 48 |  |  | SORIT 12 |  |  | 1/2
8OM |  | 8' | 8' OM-E | 1 |  | Fresh Meat | 3.84 | 22 | Off Cycle | 120 | 0.15 | 2.33 | 0.5 | 18 | 279.6 | 60 |  |  | SORIT 12 |  |  | 7/8
12OM |  | 12' | 12' OM-E | 1 |  | Fresh Meat | 5.76 | 22 | Off Cycle | 120 | 0.23 | 3.5 | 0.76 | 27.6 | 420 | 91.2 |  |  | SORIT 12 |  |  | 7/8
8'8OM |  | 8'8' | 16' OM-E | 1 |  | Fresh Meat | 7.68 | 22 | Off Cycle | 120 | 0.3 | 4.66 | 1 | 36 | 559.2 | 120 |  |  | SORIT 12 |  |  | 1 1/8
8'12OM |  | 8'12' | 20' OM-E | 1 |  | Fresh Meat | 9.6 | 22 | Off Cycle | 120 | 0.38 | 5.83 | 1.26 | 45.6 | 699.6 | 151.2 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8OM |  | 8'8'8' | 24' OM-E | 1 |  | Fresh Meat | 11.52 | 22 | Off Cycle | 120 | 0.45 | 6.99 | 1.5 | 54 | 838.8 | 180 |  |  | SORIT 15 |  |  | 1 3/8
12'12OM |  | 12'12' | 24' OM-E | 1 |  | Fresh Meat | 11.52 | 22 | Off Cycle | 120 | 0.46 | 7 | 1.52 | 55.2 | 840 | 182.4 |  |  | SORIT 15 |  |  | 1 3/8
8'8'12OM |  | 8'8'12' | 28' OM-E | 1 |  | Fresh Meat | 13.44 | 22 | Off Cycle | 120 | 0.53 | 8.16 | 1.76 | 63.6 | 979.2 | 211.2 |  |  | SORIT 20 |  |  | 1 3/8
8'8'8'8OM |  | 8'8'8'8' | 32' OM-E | 1 |  | Fresh Meat | 15.36 | 22 | Off Cycle | 120 | 0.6 | 9.32 | 2 | 72 | 1118.4 | 240 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12OM |  | 8'12'12' | 32' OM-E | 1 |  | Fresh Meat | 15.36 | 22 | Off Cycle | 120 | 0.61 | 9.33 | 2.02 | 73.2 | 1119.6 | 242.4 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12OM |  | 8'8'8'12' | 36' OM-E | 1 |  | Fresh Meat | 17.28 | 22 | Off Cycle | 120 | 0.68 | 10.49 | 2.26 | 81.6 | 1258.8 | 271.2 |  |  | SORIT 20 |  |  | 1 5/8
12'12'12OM |  | 12'12'12' | 36' OM-E | 1 |  | Fresh Meat | 17.28 | 22 | Off Cycle | 120 | 0.69 | 10.5 | 2.28 | 82.8 | 1260 | 273.6 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'8OM |  | 8'8'8'8'8' | 40' OM-E | 1 |  | Fresh Meat | 19.2 | 22 | Off Cycle | 120 | 0.75 | 11.65 | 2.5 | 90 | 1398 | 300 |  |  | SORIT 20 |  |  | 1 5/8
8'8'12'12OM |  | 8'8'12'12' | 40' OM-E | 1 |  | Fresh Meat | 19.2 | 22 | Off Cycle | 120 | 0.76 | 11.66 | 2.52 | 91.2 | 1399.2 | 302.4 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'12OM |  | 8'8'8'8'12' | 44' OM-E | 1 |  | Fresh Meat | 21.12 | 22 | Off Cycle | 120 | 0.83 | 12.82 | 2.76 | 99.6 | 1538.4 | 331.2 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12'12OM |  | 8'12'12'12' | 44' OM-E | 1 |  | Fresh Meat | 21.12 | 22 | Off Cycle | 120 | 0.84 | 12.83 | 2.78 | 100.8 | 1539.6 | 333.6 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12'12OM |  | 8'8'8'12'12' | 48' OM-E | 1 |  | Fresh Meat | 23.04 | 22 | Off Cycle | 120 | 0.91 | 13.99 | 3.02 | 109.2 | 1678.8 | 362.4 |  |  | SORIT 20 |  |  | 2 1/8
12'12'12'12OM |  | 12'12'12'12' | 48' OM-E | 1 |  | Fresh Meat | 23.04 | 22 | Off Cycle | 120 | 0.92 | 14 | 3.04 | 110.4 | 1680 | 364.8 |  |  | SORIT 20 |  |  | 2 1/8
|  | OHMH-E MD MEAT/SEAFOOD MERCHANDISER | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4OHMH |  | 4' | 4' OHMH-E | 1 |  | MD Fresh Meat | 5.36 | 22 | Off Cycle | 120 | 0.47 | 1.87 |  | 56.4 | 224.4 | 0 |  |  | SORIT 12
6OHMH |  | 6' | 6' OHMH-E | 1 |  | MD Fresh Meat | 8.04 | 22 | Off Cycle | 120 | 0.7 | 2.93 |  | 84 | 44.4 | 0 |  |  | SORIT 12
8OHMH |  | 8' | 8' OHMH-E | 1 |  | MD Fresh Meat | 10.72 | 22 | Off Cycle | 120 | 0.93 | 3.73 |  | 111.6 | 447.6 | 0 |  |  | SORIT 12 |  |  | 7/8
12OHMH |  | 12' | 12' OHMH-E | 1 |  | MD Fresh Meat | 16.08 | 22 | Off Cycle | 120 | 1.17 | 5.6 |  | 140.4 | 672 | 0 |  |  | SORIT 12 |  |  | 7/8
6'8OHMH |  | 6'8' | 14' OHMH-E | 1 |  | MD Fresh Meat | 18.76 | 22 | Off Cycle | 120 | 1.63 | 6.66 | 0 | 195.6 | 799.2 | 0 |  |  | SORIT 12
8'8OHMH |  | 8'8' | 16' OHMH-E | 1 |  | MD Fresh Meat | 21.44 | 22 | Off Cycle | 120 | 1.86 | 7.46 | 0 | 223.2 | 895.2 | 0 |  |  | SORIT 12 |  |  | 1 1/8
8'12OHMH |  | 8'12' | 20' OHMH-E | 1 |  | MD Fresh Meat | 26.8 | 22 | Off Cycle | 120 | 2.1 | 9.33 | 0 | 252 | 1119.6 | 0 |  |  | SORIT 15 |  |  | 1 1/8
8'8'8OHMH |  | 8'8'8' | 24' OHMH-E | 1 |  | MD Fresh Meat | 32.16 | 22 | Off Cycle | 120 | 2.79 | 11.19 | 0 | 334.8 | 1342.8 | 0 |  |  | SORIT 15 |  |  | 1 3/8
12'12OHMH |  | 12'12' | 24' OHMH-E | 1 |  | MD Fresh Meat | 32.16 | 22 | Off Cycle | 120 | 2.34 | 11.2 | 0 | 280.8 | 1344 | 0 |  |  | SORIT 15 |  |  | 1 3/8
8'8'12OHMH |  | 8'8'12' | 28' OHMH-E | 1 |  | MD Fresh Meat | 37.52 | 22 | Off Cycle | 120 | 3.03 | 13.06 | 0 | 363.6 | 1567.2 | 0 |  |  | SORIT 20 |  |  | 1 3/8
8'8'8'8OHMH |  | 8'8'8'8' | 32' OHMH-E | 1 |  | MD Fresh Meat | 42.88 | 22 | Off Cycle | 120 | 3.72 | 14.92 | 0 | 446.4 | 1790.4 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12OHMH |  | 8'12'12' | 32' OHMH-E | 1 |  | MD Fresh Meat | 42.88 | 22 | Off Cycle | 120 | 3.27 | 14.93 | 0 | 392.4 | 1791.6 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12OHMH |  | 8'8'8'12' | 36' OHMH-E | 1 |  | MD Fresh Meat | 48.24 | 22 | Off Cycle | 120 | 3.96 | 16.79 | 0 | 475.2 | 2014.8 | 0 |  |  | SORIT 20 |  |  | 1 5/8
12'12'12OHMH |  | 12'12'12' | 36' OHMH-E | 1 |  | MD Fresh Meat | 48.24 | 22 | Off Cycle | 120 | 3.51 | 16.8 | 0 | 421.2 | 2016 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'8OHMH |  | 8'8'8'8'8' | 40' OHMH-E | 1 |  | MD Fresh Meat | 53.6 | 22 | Off Cycle | 120 | 4.65 | 18.65 | 0 | 558 | 2238 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'12'12OHMH |  | 8'8'12'12' | 40' OHMH-E | 1 |  | MD Fresh Meat | 53.6 | 22 | Off Cycle | 120 | 4.2 | 18.66 | 0 | 504 | 2239.2 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'8'12OHMH |  | 8'8'8'8'12' | 44' OHMH-E | 1 |  | MD Fresh Meat | 58.96 | 22 | Off Cycle | 120 | 4.89 | 20.52 | 0 | 586.8 | 2462.4 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'12'12'12OHMH |  | 8'12'12'12' | 44' OHMH-E | 1 |  | MD Fresh Meat | 58.96 | 22 | Off Cycle | 120 | 4.44 | 20.53 | 0 | 532.8 | 2463.6 | 0 |  |  | SORIT 20 |  |  | 1 5/8
8'8'8'12'12OHMH |  | 8'8'8'12'12' | 48' OHMH-E | 1 |  | MD Fresh Meat | 64.32 | 22 | Off Cycle | 120 | 5.13 | 22.39 | 0 | 615.6 | 2686.8 | 0 |  |  | SORIT 20 |  |  | 2 1/8
12'12'12'12OHMH |  | 12'12'12'12' | 48' OHMH-E | 1 |  | MD Fresh Meat | 64.32 | 22 | Off Cycle | 120 | 4.68 | 22.4 | 0 | 561.6 | 2688 | 0 |  |  | SORIT 20 |  |  | 2 1/8
10PTDG |  | 10' | 10' PTDG | 1 |  | Service Seafood | 10 | 15 | Off Cycle | 120 | 1.72 | 3 |  | 206.4 | 360
10DB
|  | OHP-E PRODUCE MERCHANDISER | [15 empty] | 90
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
4OHP |  | 4' | 4' OHP-E | 1 |  | MD Produce | 3.42 | 29 | Off Cycle | 120 | 0.47 | 0.23 |  | 56.4 | 27.6 | 0
6OHP |  | 6' | 6' OHP-E | 1 |  | MD Produce | 5.13 | 29 | Off Cycle | 120 | 0.47 | 0.37 |  | 56.4 | 44.4 | 0
8OHP |  | 8' | 8' OHP-E | 1 |  | MD Produce | 6.84 | 29 | Off Cycle | 120 | 0.7 | 0.47 |  | 84 | 56.4 | 0
12OHP |  | 12' | 12' OHP-E | 1 |  | MD Produce | 10.26 | 29 | Off Cycle | 120 | 0.93 | 0.7 |  | 111.6 | 84 | 0
6'8OHP |  | 6'8' | 14' OHP-E | 1 |  | MD Produce | 11.97 | 29 | Off Cycle | 120 | 1.17 | 0.84 | 0 | 140.4 | 100.8 | 0
8'8OHP |  | 8'8' | 16' OHP-E | 1 |  | MD Produce | 13.68 | 29 | Off Cycle | 120 | 1.4 | 0.94 | 0 | 168 | 112.8 | 0
8'12OHP |  | 8'12' | 20' OHP-E | 1 |  | MD Produce | 17.1 | 29 | Off Cycle | 120 | 1.63 | 1.17 | 0 | 195.6 | 140.4 | 0
8'8'8OHP |  | 8'8'8' | 24' OHP-E | 1 |  | MD Produce | 20.52 | 29 | Off Cycle | 120 | 2.1 | 1.41 | 0 | 252 | 169.2 | 0
12'12OHP |  | 12'12' | 24' OHP-E | 1 |  | MD Produce | 20.52 | 29 | Off Cycle | 120 | 1.86 | 1.4 | 0 | 223.2 | 168 | 0
8'8'12OHP |  | 8'8'12' | 28' OHP-E | 1 |  | MD Produce | 23.94 | 29 | Off Cycle | 120 | 2.33 | 1.64 | 0 | 279.6 | 196.8 | 0
8'8'8'8OHP |  | 8'8'8'8' | 32' OHP-E | 1 |  | MD Produce | 27.36 | 29 | Off Cycle | 120 | 2.8 | 1.88 | 0 | 336 | 225.6 | 0
8'12'12OHP |  | 8'12'12 | 32' OHP-E | 1 |  | MD Produce | 27.36 | 29 | Off Cycle | 120 | 2.56 | 1.87 | 0 | 307.2 | 224.4 | 0
8'8'8'12OHP |  | 8'8'8'12' | 36' OHP-E | 1 |  | MD Produce | 30.78 | 29 | Off Cycle | 120 | 3.03 | 2.11 | 0 | 363.6 | 253.2 | 0
12'12'12OHP |  | 12'12'12' | 36' OHP-E | 1 |  | MD Produce | 30.78 | 29 | Off Cycle | 120 | 2.79 | 2.1 | 0 | 334.8 | 252 | 0
8'8'8'8'8OHP |  | 8'8'8'8'8' | 40' OHP-E | 1 |  | MD Produce | 34.2 | 29 | Off Cycle | 120 | 3.5 | 2.35 | 0 | 420 | 282 | 0
8'8'12'12OHP |  | 8'8'12'12' | 40'OHP-E | 1 |  | MD Produce | 34.2 | 29 | Off Cycle | 120 | 3.26 | 2.34 | 0 | 391.2 | 280.8 | 0
8'8'8'8'12OHP |  | 8'8'8'8'12' | 44' OHP-E | 1 |  | MD Produce | 37.62 | 29 | Off Cycle | 120 | 3.73 | 2.58 | 0 | 447.6 | 309.6 | 0
8'12'12'12OHP |  | 8'12'12'12' | 44' OHP-E | 1 |  | MD Produce | 37.62 | 29 | Off Cycle | 120 | 3.49 | 2.57 | 0 | 418.8 | 308.4 | 0
8'8'8'12'12OHP |  | 8'8'8'12'12' | 48' OHP-E | 1 |  | MD Produce | 41.04 | 29 | Off Cycle | 120 | 3.96 | 2.81 | 0 | 475.2 | 337.2 | 0
12'12'12'12OHP |  | 12'12'12'12' | 48' OHP-E | 1 |  | MD Produce | 41.04 | 29 | Off Cycle | 120 | 3.72 | 2.8 | 0 | 446.4 | 336 | 0
8'12'12'12'12OHP |  | 8'12'12'12'12 | 56' OHP-E | 1 |  | MD Produce | 47.88 | 29 | Off Cycle | 120 | 4.42 | 3.27 | 0 | 530.4 | 392.4 | 0
|  | ONRIZ | FROZEN FOOD | [7 empty] | Tnk htr amp | LED | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2ONRIZ |  | 2 | 2Dr ONRIZ | 1 |  | Frozen Food | 2.234 | -11 | HG 2 Wire | 120 | 1.3 | 0.3 | 2.1 | 156 | 36 | 252 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3ONRIZ |  | 3 | 3Dr ONRIZ | 1 |  | Frozen Food | 3.486 | -11 | HG 2 Wire | 120 | 1.5 | 0.5 | 3.2 | 180 | 60 | 384 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4ONRIZ |  | 4 | 4Dr ONRIZ | 1 |  | Frozen Food | 4.648 | -11 | HG 2 Wire | 120 | 1.9 | 0.6 | 4.2 | 228 | 72 | 504 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5ONRIZ |  | 5 | 5Dr ONRIZ | 1 |  | Frozen Food | 5.81 | -11 | HG 2 Wire | 120 | 2.3 | 0.8 | 5.2 | 276 | 96 | 624 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6ONRIZ |  | 6 | 6Dr ONRIZ | 1 |  | Frozen Food | 6.972 | -11 | HG 2 Wire | 120 | 2.7 | 1 | 6.2 | 324 | 120 | 744 | E14S250 |  | SORIT 12
3,3ONRIZ |  | 3,3 | 6Dr ONRIZ | 1 |  | Frozen Food | 6.972 | -11 | HG 2 Wire | 120 | 3 | 1 | 6.4 | 360 | 120 | 768 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3ONRIZ |  | 4,3 | 7Dr ONRIZ | 1 |  | Frozen Food | 8.134 | -11 | HG 2 Wire | 120 | 3.4 | 1.1 | 7.4 | 408 | 132 | 888 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4ONRIZ |  | 4,4 | 8Dr ONRIZ | 1 |  | Frozen Food | 9.296 | -11 | HG 2 Wire | 120 | 3.8 | 1.2 | 8.4 | 456 | 144 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3ONRIZ |  | 5,3 | 8Dr ONRIZ | 1 |  | Frozen Food | 9.296 | -11 | HG 2 Wire | 120 | 3.8 | 1.3 | 8.4 | 456 | 156 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4ONRIZ |  | 5,4 | 9Dr ONRIZ | 1 |  | Frozen Food | 10.458 | -11 | HG 2 Wire | 120 | 4.2 | 1.4 | 9.4 | 504 | 168 | 1128 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
3,3,3ONRIZ |  | 3,3,3 | 9Dr ONRIZ | 1 |  | Frozen Food | 10.458 | -11 | HG 2 Wire | 120 | 4.5 | 1.5 | 9.6 | 540 | 180 | 1152 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5ONRIZ |  | 5,5 | 10Dr ONRIZ | 1 |  | Frozen Food | 11.62 | -11 | HG 2 Wire | 120 | 4.6 | 1.6 | 10.4 | 552 | 192 | 1248 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,3,3ONRIZ |  | 4,3,3 | 10Dr ONRIZ | 1 |  | Frozen Food | 11.62 | -11 | HG 2 Wire | 120 | 4.9 | 1.6 | 10.6 | 588 | 192 | 1272 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,3,3ONRIZ |  | 5,3,3 | 11Dr ONRIZ | 1 |  | Frozen Food | 12.782 | -11 | HG 2 Wire | 120 | 5.3 | 1.8 | 11.6 | 636 | 216 | 1392 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,4,3ONRIZ |  | 4,4,3 | 11Dr ONRIZ | 1 |  | Frozen Food | 12.782 | -11 | HG 2 Wire | 120 | 5.3 | 1.7 | 11.6 | 636 | 204 | 1392 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,4,4ONRIZ |  | 4,4,4 | 12Dr ONRIZ | 1 |  | Frozen Food | 13.944 | -11 | HG 2 Wire | 120 | 5.7 | 1.8 | 12.6 | 684 | 216 | 1512 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,4,3ONRIZ |  | 5,4,3 | 12Dr ONRIZ | 1 |  | Frozen Food | 13.944 | -11 | HG 2 Wire | 120 | 5.7 | 1.9 | 12.6 | 684 | 228 | 1512 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,4,4ONRIZ |  | 5,4,4 | 13Dr ONRIZ | 1 |  | Frozen Food | 15.106 | -11 | HG 2 Wire | 120 | 6.1 | 2 | 13.6 | 732 | 240 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3ONRIZ |  | 5,5,3 | 13Dr ONRIZ | 1 |  | Frozen Food | 15.106 | -11 | HG 2 Wire | 120 | 6.1 | 2.1 | 13.6 | 732 | 252 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4ONRIZ |  | 5,5,4 | 14Dr ONRIZ | 1 |  | Frozen Food | 16.268 | -11 | HG 2 Wire | 120 | 6.5 | 2.2 | 14.6 | 780 | 264 | 1752 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,3,3ONRIZ |  | 4,4,3,3 | 14Dr ONRIZ | 1 |  | Frozen Food | 16.268 | -11 | HG 2 Wire | 120 | 6.8 | 2.2 | 14.8 | 816 | 264 | 1776 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,5ONRIZ |  | 5,5,5 | 15Dr ONRIZ | 1 |  | Frozen Food | 17.43 | -11 | HG 2 Wire | 120 | 6.9 | 2.4 | 15.6 | 828 | 288 | 1872 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,3ONRIZ |  | 4,4,4,3 | 15Dr ONRIZ | 1 |  | Frozen Food | 17.43 | -11 | HG 2 Wire | 120 | 7.2 | 2.3 | 15.8 | 864 | 276 | 1896 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,3,3ONRIZ |  | 5,5,3,3 | 16Dr ONRIZ | 1 |  | Frozen Food | 18.592 | -11 | HG 2 Wire | 120 | 7.6 | 2.6 | 16.8 | 912 | 312 | 2016 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,4ONRIZ |  | 4,4,4,4 | 16Dr ONRIZ | 1 |  | Frozen Food | 18.592 | -11 | HG 2 Wire | 120 | 7.6 | 2.4 | 16.8 | 912 | 288 | 2016 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
|  | ONIZ | NARROW ISLAND FROZEN FOOD | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8ONIZ |  | 8' | 8' ONIZ | 1 |  | Frozen Food | 3.52 | -12 | HG 2 Wire | 120 | 0.3 |  | 0.75 | 36 |  | 90 | E14S250 |  | SORIT 12 |  |  | 7/8
12ONIZ |  | 12' | 12' ONIZ | 1 |  | Frozen Food | 5.28 | -12 | HG 2 Wire | 120 | 0.45 |  | 1.42 | 54 |  | 170.4 | E14S250 |  | SORIT 12 |  |  | 7/8
8'8ONIZ |  | 8'8' | 16' ONIZ | 1 |  | Frozen Food | 7.04 | -12 | HG 2 Wire | 120 | 0.6 |  | 1.5 | 72 |  | 180 | E14S250 |  | SORIT 12 |  |  | 1 1/8
8'12ONIZ |  | 8'12' | 20' ONIZ | 1 |  | Frozen Food | 8.8 | -12 | HG 2 Wire | 120 | 0.75 |  | 2.17 | 90 |  | 260.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8
8'8'8ONIZ |  | 8'8'8' | 24' ONIZ | 1 |  | Frozen Food | 10.56 | -12 | HG 2 Wire | 120 | 0.9 |  | 2.25 | 108 |  | 270 | E14S250 |  | SORIT 12 |  |  | 1 3/8
12'12ONIZ |  | 12'12' | 24' ONIZ | 1 |  | Frozen Food | 10.56 | -12 | HG 2 Wire | 120 | 0.9 |  | 2.84 | 108 |  | 340.8 | E14S250 |  | SORIT 12 |  |  | 1 3/8
8'8'12ONIZ |  | 8'8'12' | 28' ONIZ | 1 |  | Frozen Food | 12.32 | -12 | HG 2 Wire | 120 | 1.05 |  | 2.92 | 126 |  | 350.4 | E14S250 |  | SORIT 12 |  |  | 1 3/8
8'12'12ONIZ |  | 8'12'12' | 32' ONIZ | 1 |  | Frozen Food | 14.08 | -12 | HG 2 Wire | 120 | 1.2 |  | 3.59 | 144 |  | 430.8 | E14S250 |  | SORIT 12 |  |  | 1 5/8
8'8'8'12ONIZ |  | 8'8'8'12' | 36' ONIZ | 1 |  | Frozen Food | 15.84 | -12 | HG 2 Wire | 120 | 1.05 |  | 3.67 | 126 |  | 440.4 | E14S250 |  | SORIT 12 |  |  | 1 5/8
12'12'12ONIZ |  | 12'12'12' | 36' ONIZ | 1 |  | Frozen Food | 15.84 | -12 | HG 2 Wire | 120 | 1.35 |  | 4.26 | 162 |  | 511.2 | E14S250 |  | SORIT 12 |  |  | 1 5/8
|  | ONIZ | NARROW ISLAND ICE CREAM | [14 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
8ONIZ |  | 8' | 8' ONIZ | 1 |  | Ice Cream | 4 | -22 | HG 2 Wire | 120 | 0.3 |  | 0.75 | 36 |  | 90 | E14S250 |  | SORIT 12 |  |  | 7/8
12ONIZ |  | 12' | 12' ONIZ | 1 |  | Ice Cream | 6 | -22 | HG 2 Wire | 120 | 0.45 |  | 1.42 | 54 |  | 170.4 | E14S250 |  | SORIT 12 |  |  | 7/8
8'8ONIZ |  | 8'8' | 16' ONIZ | 1 |  | Ice Cream | 8 | -22 | HG 2 Wire | 120 | 0.6 |  | 1.5 | 72 |  | 180 | E14S250 |  | SORIT 12 |  |  | 1 1/8
8'12ONIZ |  | 8'12' | 20' ONIZ | 1 |  | Ice Cream | 10 | -22 | HG 2 Wire | 120 | 0.75 |  | 2.17 | 90 |  | 260.4 | E14S250 |  | SORIT 12 |  |  | 1 1/8
8'8'8ONIZ |  | 8'8'8' | 24' ONIZ | 1 |  | Ice Cream | 12 | -22 | HG 2 Wire | 120 | 0.9 |  | 2.25 | 108 |  | 270 | E14S250 |  | SORIT 12 |  |  | 1 3/8
12'12ONIZ |  | 12'12' | 24' ONIZ | 1 |  | Ice Cream | 12 | -22 | HG 2 Wire | 120 | 0.9 |  | 2.84 | 108 |  | 340.8 | E14S250 |  | SORIT 12 |  |  | 1 3/8
8'8'12ONIZ |  | 8'8'12' | 28' ONIZ | 1 |  | Ice Cream | 14 | -22 | HG 2 Wire | 120 | 1.05 |  | 2.92 | 126 |  | 350.4 | E14S250 |  | SORIT 15 |  |  | 1 3/8
8'12'12ONIZ |  | 8'12'12' | 32' ONIZ | 1 |  | Ice Cream | 16 | -22 | HG 2 Wire | 120 | 1.2 |  | 3.59 | 144 |  | 430.8 | E14S250 |  | SORIT 15 |  |  | 1 5/8
8'8'8'12ONIZ |  | 8'8'8'12' | 36' ONIZ | 1 |  | Ice Cream | 18 | -22 | HG 2 Wire | 120 | 1.05 |  | 3.67 | 126 |  | 440.4 | E14S250 |  | SORIT 15 |  |  | 1 5/8
12'12'12ONIZ |  | 12'12'12' | 36' ONIZ | 1 |  | Ice Cream | 18 | -22 | HG 2 Wire | 120 | 1.35 |  | 4.26 | 162 |  | 511.2 | E14S250 |  | SORIT 15 |  |  | 1 5/8
|  | ORZ-E | Frozen Food | [7 empty] | Tnk htr amp | [6 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2ORZ |  | 2 | 2Dr ORZ | 1 |  | Frozen Food | 2.69 | -11 | HG 2 Wire | 120 | 1.3 | 1.5 | 2.1 | 156 | 180 | 252 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3ORZ |  | 3 | 3Dr ORZ | 1 |  | Frozen Food | 4.03 | -11 | HG 2 Wire | 120 | 1.5 | 1.9 | 3.2 | 180 | 228 | 384 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4ORZ |  | 4 | 4Dr ORZ | 1 |  | Frozen Food | 5.38 | -11 | HG 2 Wire | 120 | 1.9 | 2.4 | 4.2 | 228 | 288 | 504 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5ORZ |  | 5 | 5Dr ORZ | 1 |  | Frozen Food | 6.72 | -11 | HG 2 Wire | 120 | 2.3 | 2.9 | 5.2 | 276 | 348 | 624 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6ORZ |  | 6 | 6Dr ORZ | 1 |  | Frozen Food | 8.07 | -11 | HG 2 Wire | 120 | 2.7 | 3.4 | 6.2 | 324 | 408 | 744 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3ORZ |  | 3,3 | 6Dr ORZ | 1 |  | Frozen Food | 8.06 | -11 | HG 2 Wire | 120 | 3 | 3.8 | 6.4 | 360 | 456 | 768 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3ORZ |  | 4,3 | 7Dr ORZ | 1 |  | Frozen Food | 9.41 | -11 | HG 2 Wire | 120 | 3.4 | 4.3 | 7.4 | 408 | 516 | 888 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4ORZ |  | 4,4 | 8Dr ORZ | 1 |  | Frozen Food | 10.76 | -11 | HG 2 Wire | 120 | 3.8 | 4.8 | 8.4 | 456 | 576 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3ORZ |  | 5,3 | 8Dr ORZ | 1 |  | Frozen Food | 10.75 | -11 | HG 2 Wire | 120 | 3.8 | 4.8 | 8.4 | 456 | 576 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4ORZ |  | 5,4 | 9Dr ORZ | 1 |  | Frozen Food | 12.1 | -11 | HG 2 Wire | 120 | 4.2 | 5.3 | 9.4 | 504 | 636 | 1128 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
3,3,3ORZ |  | 3,3,3 | 9Dr ORZ | 1 |  | Frozen Food | 12.09 | -11 | HG 2 Wire | 120 | 4.5 | 5.7 | 9.6 | 540 | 684 | 1152 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5ORZ |  | 5,5 | 10Dr ORZ | 1 |  | Frozen Food | 13.44 | -11 | HG 2 Wire | 120 | 4.6 | 5.8 | 10.4 | 552 | 696 | 1248 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,3,3ORZ |  | 4,3,3 | 10Dr ORZ | 1 |  | Frozen Food | 13.44 | -11 | HG 2 Wire | 120 | 4.9 | 6.2 | 10.6 | 588 | 744 | 1272 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3ORZ |  | 5,3,3 | 11Dr ORZ | 1 |  | Frozen Food | 14.78 | -11 | HG 2 Wire | 120 | 5.3 | 6.7 | 11.6 | 636 | 804 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3ORZ |  | 4,4,3 | 11Dr ORZ | 1 |  | Frozen Food | 14.79 | -11 | HG 2 Wire | 120 | 5.3 | 6.7 | 11.6 | 636 | 804 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4ORZ |  | 4,4,4 | 12Dr ORZ | 1 |  | Frozen Food | 16.14 | -11 | HG 2 Wire | 120 | 5.7 | 7.2 | 12.6 | 684 | 864 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3ORZ |  | 5,4,3 | 12Dr ORZ | 1 |  | Frozen Food | 16.13 | -11 | HG 2 Wire | 120 | 5.7 | 7.2 | 12.6 | 684 | 864 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2ORZ |  | 4,4,3,2 | 13Dr ORZ | 1 |  | Frozen Food | 17.48 | -11 | HG 2 Wire | 120 | 6.6 | 8.2 | 13.7 | 792 | 984 | 1644 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4ORZ |  | 5,4,4 | 13Dr ORZ | 1 |  | Frozen Food | 17.48 | -11 | HG 2 Wire | 120 | 6.1 | 7.7 | 13.6 | 732 | 924 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3ORZ |  | 5,5,3 | 13Dr ORZ | 1 |  | Frozen Food | 17.47 | -11 | HG 2 Wire | 120 | 6.1 | 7.7 | 13.6 | 732 | 924 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4ORZ |  | 5,5,4 | 14Dr ORZ | 1 |  | Frozen Food | 18.82 | -11 | HG 2 Wire | 120 | 6.5 | 8.2 | 14.6 | 780 | 984 | 1752 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,3,3ORZ |  | 4,4,3,3 | 14Dr ORZ | 1 |  | Frozen Food | 18.82 | -11 | HG 2 Wire | 120 | 6.8 | 8.6 | 14.8 | 816 | 1032 | 1776 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,5ORZ |  | 5,5,5 | 15Dr ORZ | 1 |  | Frozen Food | 20.16 | -11 | HG 2 Wire | 120 | 6.9 | 8.7 | 15.6 | 828 | 1044 | 1872 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,3ORZ |  | 4,4,4,3 | 15Dr ORZ | 1 |  | Frozen Food | 20.17 | -11 | HG 2 Wire | 120 | 7.2 | 9.1 | 15.8 | 864 | 1092 | 1896 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,3,3ORZ |  | 5,5,3,3 | 16Dr ORZ | 1 |  | Frozen Food | 21.5 | -11 | HG 2 Wire | 120 | 7.6 | 9.6 | 16.8 | 912 | 1152 | 2016 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,4ORZ |  | 4,4,4,4 | 16Dr ORZ | 1 |  | Frozen Food | 21.52 | -11 | HG 2 Wire | 120 | 7.6 | 9.6 | 16.8 | 912 | 1152 | 2016 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
|  | ORZ-E | Ice Cream | [7 empty] | Tnk htr amp | T8 | [5 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2ORZIC |  | 2 | 2Dr ORZ | 1 |  | Ice Cream | 2.81 | -17 | HG 2 Wire | 120 | 1.3 | 1.5 | 2.1 | 156 | 180 | 252 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3ORZIC |  | 3 | 3Dr ORZ | 1 |  | Ice Cream | 4.21 | -17 | HG 2 Wire | 120 | 1.5 | 1.9 | 3.2 | 180 | 228 | 384 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4ORZIC |  | 4 | 4Dr ORZ | 1 |  | Ice Cream | 5.62 | -17 | HG 2 Wire | 120 | 1.9 | 2.4 | 4.2 | 228 | 288 | 504 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5ORZIC |  | 5 | 5Dr ORZ | 1 |  | Ice Cream | 7.02 | -17 | HG 2 Wire | 120 | 2.3 | 2.9 | 5.2 | 276 | 348 | 624 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6ORZIC |  | 6 | 6Dr ORZ | 1 |  | Ice Cream | 8.43 | -17 | HG 2 Wire | 120 | 2.7 | 3.4 | 6.2 | 324 | 408 | 744 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3ORZIC |  | 3,3 | 6Dr ORZ | 1 |  | Ice Cream | 8.42 | -17 | HG 2 Wire | 120 | 3 | 3.8 | 6.4 | 360 | 456 | 768 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3ORZIC |  | 4,3 | 7Dr ORZ | 1 |  | Ice Cream | 9.83 | -17 | HG 2 Wire | 120 | 3.4 | 4.3 | 7.4 | 408 | 516 | 888 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4ORZIC |  | 4,4 | 8Dr ORZ | 1 |  | Ice Cream | 11.24 | -17 | HG 2 Wire | 120 | 3.8 | 4.8 | 8.4 | 456 | 576 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3ORZIC |  | 5,3 | 8Dr ORZ | 1 |  | Ice Cream | 11.23 | -17 | HG 2 Wire | 120 | 3.8 | 4.8 | 8.4 | 456 | 576 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4ORZIC |  | 5,4 | 9Dr ORZ | 1 |  | Ice Cream | 12.64 | -17 | HG 2 Wire | 120 | 4.2 | 5.3 | 9.4 | 504 | 636 | 1128 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
3,3,3ORZIC |  | 3,3,3 | 9Dr ORZ | 1 |  | Ice Cream | 12.63 | -17 | HG 2 Wire | 120 | 4.5 | 5.7 | 9.6 | 540 | 684 | 1152 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5ORZIC |  | 5,5 | 10Dr ORZ | 1 |  | Ice Cream | 14.04 | -17 | HG 2 Wire | 120 | 4.6 | 5.8 | 10.4 | 552 | 696 | 1248 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3ORZIC |  | 4,3,3 | 10Dr ORZ | 1 |  | Ice Cream | 14.04 | -17 | HG 2 Wire | 120 | 4.9 | 6.2 | 10.6 | 588 | 744 | 1272 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3ORZIC |  | 5,3,3 | 11Dr ORZ | 1 |  | Ice Cream | 15.44 | -17 | HG 2 Wire | 120 | 5.3 | 6.7 | 11.6 | 636 | 804 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3ORZIC |  | 4,4,3 | 11Dr ORZ | 1 |  | Ice Cream | 15.45 | -17 | HG 2 Wire | 120 | 5.3 | 6.7 | 11.6 | 636 | 804 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4ORZIC |  | 4,4,4 | 12Dr ORZ | 1 |  | Ice Cream | 16.86 | -17 | HG 2 Wire | 120 | 5.7 | 7.2 | 12.6 | 684 | 864 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3ORZIC |  | 5,4,3 | 12Dr ORZ | 1 |  | Ice Cream | 16.85 | -17 | HG 2 Wire | 120 | 5.7 | 7.2 | 12.6 | 684 | 864 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2ORZIC |  | 4,4,3,2 | 13Dr ORZ | 1 |  | Ice Cream | 18.26 | -17 | HG 2 Wire | 120 | 6.6 | 8.2 | 13.7 | 792 | 984 | 1644 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4ORZIC |  | 5,4,4 | 13Dr ORZ | 1 |  | Ice Cream | 18.26 | -17 | HG 2 Wire | 120 | 6.1 | 7.7 | 13.6 | 732 | 924 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3ORZIC |  | 5,5,3 | 13Dr ORZ | 1 |  | Ice Cream | 18.25 | -17 | HG 2 Wire | 120 | 6.1 | 7.7 | 13.6 | 732 | 924 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4ORZIC |  | 5,5,4 | 14Dr ORZ | 1 |  | Ice Cream | 19.66 | -17 | HG 2 Wire | 120 | 6.5 | 8.2 | 14.6 | 780 | 984 | 1752 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,3,3ORZIC |  | 4,4,3,3 | 14Dr ORZ | 1 |  | Ice Cream | 19.66 | -17 | HG 2 Wire | 120 | 6.8 | 8.6 | 14.8 | 816 | 1032 | 1776 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,5ORZIC |  | 5,5,5 | 15Dr ORZ | 1 |  | Ice Cream | 21.06 | -17 | HG 2 Wire | 120 | 6.9 | 8.7 | 15.6 | 828 | 1044 | 1872 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3ORZIC |  | 4,4,4,3 | 15Dr ORZ | 1 |  | Ice Cream | 21.07 | -17 | HG 2 Wire | 120 | 7.2 | 9.1 | 15.8 | 864 | 1092 | 1896 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3ORZIC |  | 5,5,3,3 | 16Dr ORZ | 1 |  | Ice Cream | 22.46 | -17 | HG 2 Wire | 120 | 7.6 | 9.6 | 16.8 | 912 | 1152 | 2016 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4ORZIC |  | 4,4,4,4 | 16Dr ORZ | 1 |  | Ice Cream | 22.48 | -17 | HG 2 Wire | 120 | 7.6 | 9.6 | 16.8 | 912 | 1152 | 2016 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | ORZ-ELMD | Frozen Food | [7 empty] | Tnk htr amp | [6 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2ORZLED |  | 2 | 2Dr ORZ LED | 1 |  | Frozen Food | 2.028 | -7 | HG 2 Wire | 120 | 1.3 | 0.3 | 2.1 | 156 | 36 | 252 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3ORZLED |  | 3 | 3Dr ORZ LED | 1 |  | Frozen Food | 3.042 | -7 | HG 2 Wire | 120 | 1.5 | 0.5 | 3.2 | 180 | 60 | 384 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4ORZLED |  | 4 | 4Dr ORZ LED | 1 |  | Frozen Food | 4.056 | -7 | HG 2 Wire | 120 | 1.9 | 0.6 | 4.2 | 228 | 72 | 504 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5ORZLED |  | 5 | 5Dr ORZ LED | 1 |  | Frozen Food | 5.07 | -7 | HG 2 Wire | 120 | 2.3 | 0.8 | 5.2 | 276 | 96 | 624 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6ORZLED |  | 6 | 6Dr ORZ LED | 1 |  | Frozen Food | 6.084 | -7 | HG 2 Wire | 120 | 2.7 | 1 | 6.2 | 324 | 120 | 744 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3ORZLED |  | 3,3 | 6Dr ORZ LED | 1 |  | Frozen Food | 6.084 | -7 | HG 2 Wire | 120 | 3 | 1 | 6.4 | 360 | 120 | 768 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3ORZLED |  | 4,3 | 7Dr ORZ LED | 1 |  | Frozen Food | 7.098 | -7 | HG 2 Wire | 120 | 3.4 | 1.1 | 7.4 | 408 | 132 | 888 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4ORZLED |  | 4,4 | 8Dr ORZ LED | 1 |  | Frozen Food | 8.112 | -7 | HG 2 Wire | 120 | 3.8 | 1.2 | 8.4 | 456 | 144 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3ORZLED |  | 5,3 | 8Dr ORZ LED | 1 |  | Frozen Food | 8.112 | -7 | HG 2 Wire | 120 | 3.8 | 1.3 | 8.4 | 456 | 156 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4ORZLED |  | 5,4 | 9Dr ORZ LED | 1 |  | Frozen Food | 9.126 | -7 | HG 2 Wire | 120 | 4.2 | 1.4 | 9.4 | 504 | 168 | 1128 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
3,3,3ORZLED |  | 3,3,3 | 9Dr ORZ LED | 1 |  | Frozen Food | 9.126 | -7 | HG 2 Wire | 120 | 4.5 | 1.5 | 9.6 | 540 | 180 | 1152 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5ORZLED |  | 5,5 | 10Dr ORZ LED | 1 |  | Frozen Food | 10.14 | -7 | HG 2 Wire | 120 | 4.6 | 1.6 | 10.4 | 552 | 192 | 1248 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,3,3ORZLED |  | 4,3,3 | 10Dr ORZ LED | 1 |  | Frozen Food | 10.14 | -7 | HG 2 Wire | 120 | 4.9 | 1.6 | 10.6 | 588 | 192 | 1272 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3ORZLED |  | 5,3,3 | 11Dr ORZ LED | 1 |  | Frozen Food | 11.154 | -7 | HG 2 Wire | 120 | 5.3 | 1.8 | 11.6 | 636 | 216 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3ORZLED |  | 4,4,3 | 11Dr ORZ LED | 1 |  | Frozen Food | 11.154 | -7 | HG 2 Wire | 120 | 5.3 | 1.7 | 11.6 | 636 | 204 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4ORZLED |  | 4,4,4 | 12Dr ORZ LED | 1 |  | Frozen Food | 12.168 | -7 | HG 2 Wire | 120 | 5.7 | 1.8 | 12.6 | 684 | 216 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3ORZLED |  | 5,4,3 | 12Dr ORZ LED | 1 |  | Frozen Food | 12.168 | -7 | HG 2 Wire | 120 | 5.7 | 1.9 | 12.6 | 684 | 228 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2ORZLED |  | 4,4,3,2 | 13Dr ORZ LED | 1 |  | Frozen Food | 13.182 | -7 | HG 2 Wire | 120 | 6.6 | 2 | 13.7 | 792 | 240 | 1644 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4ORZLED |  | 5,4,4 | 13Dr ORZ LED | 1 |  | Frozen Food | 13.182 | -7 | HG 2 Wire | 120 | 6.1 | 2 | 13.6 | 732 | 240 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3ORZLED |  | 5,5,3 | 13Dr ORZ LED | 1 |  | Frozen Food | 13.182 | -7 | HG 2 Wire | 120 | 6.1 | 2.1 | 13.6 | 732 | 252 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4ORZLED |  | 5,5,4 | 14Dr ORZ LED | 1 |  | Frozen Food | 14.196 | -7 | HG 2 Wire | 120 | 6.5 | 2.2 | 14.6 | 780 | 264 | 1752 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,3,3ORZLED |  | 4,4,3,3 | 14Dr ORZ LED | 1 |  | Frozen Food | 14.196 | -7 | HG 2 Wire | 120 | 6.8 | 2.2 | 14.8 | 816 | 264 | 1776 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,5ORZLED |  | 5,5,5 | 15Dr ORZ LED | 1 |  | Frozen Food | 15.21 | -7 | HG 2 Wire | 120 | 6.9 | 2.4 | 15.6 | 828 | 288 | 1872 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,3ORZLED |  | 4,4,4,3 | 15Dr ORZ LED | 1 |  | Frozen Food | 15.21 | -7 | HG 2 Wire | 120 | 7.2 | 2.3 | 15.8 | 864 | 276 | 1896 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,3,3ORZLED |  | 5,5,3,3 | 16Dr ORZ LED | 1 |  | Frozen Food | 16.224 | -7 | HG 2 Wire | 120 | 7.6 | 2.6 | 16.8 | 912 | 312 | 2016 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,4ORZLED |  | 4,4,4,4 | 16Dr ORZ LED | 1 |  | Frozen Food | 16.224 | -7 | HG 2 Wire | 120 | 7.6 | 2.4 | 16.8 | 912 | 288 | 2016 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
|  | ORZ-ELMD | Ice Cream | [7 empty] | Tnk htr amp | [6 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2ORZICLED |  | 2 | 2Dr ORZ LED | 1 |  | Ice Cream | 2.12 | -15 | HG 2 Wire | 120 | 1.3 | 0.3 | 2.1 | 156 | 36 | 252 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3ORZICLED |  | 3 | 3Dr ORZ LED | 1 |  | Ice Cream | 3.18 | -15 | HG 2 Wire | 120 | 1.5 | 0.5 | 3.2 | 180 | 60 | 384 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4ORZICLED |  | 4 | 4Dr ORZ LED | 1 |  | Ice Cream | 4.24 | -15 | HG 2 Wire | 120 | 1.9 | 0.6 | 4.2 | 228 | 72 | 504 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5ORZICLED |  | 5 | 5Dr ORZ LED | 1 |  | Ice Cream | 5.3 | -15 | HG 2 Wire | 120 | 2.3 | 0.8 | 5.2 | 276 | 96 | 624 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6ORZICLED |  | 6 | 6Dr ORZ LED | 1 |  | Ice Cream | 6.36 | -15 | HG 2 Wire | 120 | 2.7 | 1 | 6.2 | 324 | 120 | 744 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3ORZICLED |  | 3,3 | 6Dr ORZ LED | 1 |  | Ice Cream | 6.36 | -15 | HG 2 Wire | 120 | 3 | 1 | 6.4 | 360 | 120 | 768 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3ORZICLED |  | 4,3 | 7Dr ORZ LED | 1 |  | Ice Cream | 7.42 | -15 | HG 2 Wire | 120 | 3.4 | 1.1 | 7.4 | 408 | 132 | 888 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4ORZICLED |  | 4,4 | 8Dr ORZ LED | 1 |  | Ice Cream | 8.48 | -15 | HG 2 Wire | 120 | 3.8 | 1.2 | 8.4 | 456 | 144 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3ORZICLED |  | 5,3 | 8Dr ORZ LED | 1 |  | Ice Cream | 8.48 | -15 | HG 2 Wire | 120 | 3.8 | 1.3 | 8.4 | 456 | 156 | 1008 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4ORZICLED |  | 5,4 | 9Dr ORZ LED | 1 |  | Ice Cream | 9.54 | -15 | HG 2 Wire | 120 | 4.2 | 1.4 | 9.4 | 504 | 168 | 1128 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
3,3,3ORZICLED |  | 3,3,3 | 9Dr ORZ LED | 1 |  | Ice Cream | 9.54 | -15 | HG 2 Wire | 120 | 4.5 | 1.5 | 9.6 | 540 | 180 | 1152 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5ORZICLED |  | 5,5 | 10Dr ORZ LED | 1 |  | Ice Cream | 10.6 | -15 | HG 2 Wire | 120 | 4.6 | 1.6 | 10.4 | 552 | 192 | 1248 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3ORZICLED |  | 4,3,3 | 10Dr ORZ LED | 1 |  | Ice Cream | 10.6 | -15 | HG 2 Wire | 120 | 4.9 | 1.6 | 10.6 | 588 | 192 | 1272 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3ORZICLED |  | 5,3,3 | 11Dr ORZ LED | 1 |  | Ice Cream | 11.66 | -15 | HG 2 Wire | 120 | 5.3 | 1.8 | 11.6 | 636 | 216 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3ORZICLED |  | 4,4,3 | 11Dr ORZ LED | 1 |  | Ice Cream | 11.66 | -15 | HG 2 Wire | 120 | 5.3 | 1.7 | 11.6 | 636 | 204 | 1392 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4ORZICLED |  | 4,4,4 | 12Dr ORZ LED | 1 |  | Ice Cream | 12.72 | -15 | HG 2 Wire | 120 | 5.7 | 1.8 | 12.6 | 684 | 216 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3ORZICLED |  | 5,4,3 | 12Dr ORZ LED | 1 |  | Ice Cream | 12.72 | -15 | HG 2 Wire | 120 | 5.7 | 1.9 | 12.6 | 684 | 228 | 1512 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2ORZICLED |  | 4,4,3,2 | 13Dr ORZ LED | 1 |  | Ice Cream | 13.78 | -15 | HG 2 Wire | 120 | 6.6 | 2 | 13.7 | 792 | 240 | 1644 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4ORZICLED |  | 5,4,4 | 13Dr ORZ LED | 1 |  | Ice Cream | 13.78 | -15 | HG 2 Wire | 120 | 6.1 | 2 | 13.6 | 732 | 240 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3ORZICLED |  | 5,5,3 | 13Dr ORZ LED | 1 |  | Ice Cream | 13.78 | -15 | HG 2 Wire | 120 | 6.1 | 2.1 | 13.6 | 732 | 252 | 1632 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4ORZICLED |  | 5,5,4 | 14Dr ORZ LED | 1 |  | Ice Cream | 14.84 | -15 | HG 2 Wire | 120 | 6.5 | 2.2 | 14.6 | 780 | 264 | 1752 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,3,3ORZICLED |  | 4,4,3,3 | 14Dr ORZ LED | 1 |  | Ice Cream | 14.84 | -15 | HG 2 Wire | 120 | 6.8 | 2.2 | 14.8 | 816 | 264 | 1776 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,5ORZICLED |  | 5,5,5 | 15Dr ORZ LED | 1 |  | Ice Cream | 15.9 | -15 | HG 2 Wire | 120 | 6.9 | 2.4 | 15.6 | 828 | 288 | 1872 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3ORZICLED |  | 4,4,4,3 | 15Dr ORZ LED | 1 |  | Ice Cream | 15.9 | -15 | HG 2 Wire | 120 | 7.2 | 2.3 | 15.8 | 864 | 276 | 1896 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3ORZICLED |  | 5,5,3,3 | 16Dr ORZ LED | 1 |  | Ice Cream | 16.96 | -15 | HG 2 Wire | 120 | 7.6 | 2.6 | 16.8 | 912 | 312 | 2016 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4ORZICLED |  | 4,4,4,4 | 16Dr ORZ LED | 1 |  | Ice Cream | 16.96 | -15 | HG 2 Wire | 120 | 7.6 | 2.4 | 16.8 | 912 | 288 | 2016 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  | ORZH-ELMD | Frozen Food | [7 empty] | Tnk htr amp | [6 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2ORZH |  | 2 | 2Dr ORZH | 1 |  | Frozen Food | 2.028 | -7 | HG 2 Wire | 120 | 1.3 | 0.3 | 2.2 | 156 | 36 | 264 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3ORZH |  | 3 | 3Dr ORZH | 1 |  | Frozen Food | 3.042 | -7 | HG 2 Wire | 120 | 1.5 | 0.5 | 3.3 | 180 | 60 | 396 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4ORZH |  | 4 | 4Dr ORZH | 1 |  | Frozen Food | 4.056 | -7 | HG 2 Wire | 120 | 1.9 | 0.6 | 4.3 | 228 | 72 | 516 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5ORZH |  | 5 | 5Dr ORZH | 1 |  | Frozen Food | 5.07 | -7 | HG 2 Wire | 120 | 2.3 | 0.8 | 5.4 | 276 | 96 | 648 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6ORZH |  | 6 | 6Dr ORZH | 1 |  | Frozen Food | 6.084 | -7 | HG 2 Wire | 120 | 2.7 | 1 | 6.4 | 324 | 120 | 768 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3ORZH |  | 3,3 | 6Dr ORZH | 1 |  | Frozen Food | 6.084 | -7 | HG 2 Wire | 120 | 3 | 1 | 6.6 | 360 | 120 | 792 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3ORZH |  | 4,3 | 7Dr ORZH | 1 |  | Frozen Food | 7.098 | -7 | HG 2 Wire | 120 | 3.4 | 1.1 | 7.6 | 408 | 132 | 912 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4ORZH |  | 4,4 | 8Dr ORZH | 1 |  | Frozen Food | 8.112 | -7 | HG 2 Wire | 120 | 3.8 | 1.2 | 8.6 | 456 | 144 | 1032 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3ORZH |  | 5,3 | 8Dr ORZH | 1 |  | Frozen Food | 8.112 | -7 | HG 2 Wire | 120 | 3.8 | 1.3 | 8.7 | 456 | 156 | 1044 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4ORZH |  | 5,4 | 9Dr ORZH | 1 |  | Frozen Food | 9.126 | -7 | HG 2 Wire | 120 | 4.2 | 1.4 | 9.7 | 504 | 168 | 1164 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
3,3,3ORZH |  | 3,3,3 | 9Dr ORZH | 1 |  | Frozen Food | 9.126 | -7 | HG 2 Wire | 120 | 4.5 | 1.5 | 9.9 | 540 | 180 | 1188 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5ORZH |  | 5,5 | 10Dr ORZH | 1 |  | Frozen Food | 10.14 | -7 | HG 2 Wire | 120 | 4.6 | 1.6 | 10.8 | 552 | 192 | 1296 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
4,3,3ORZH |  | 4,3,3 | 10Dr ORZH | 1 |  | Frozen Food | 10.14 | -7 | HG 2 Wire | 120 | 4.9 | 1.6 | 10.9 | 588 | 192 | 1308 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3ORZH |  | 5,3,3 | 11Dr ORZH | 1 |  | Frozen Food | 11.154 | -7 | HG 2 Wire | 120 | 5.3 | 1.8 | 12 | 636 | 216 | 1440 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3ORZH |  | 4,4,3 | 11Dr ORZH | 1 |  | Frozen Food | 11.154 | -7 | HG 2 Wire | 120 | 5.3 | 1.7 | 11.9 | 636 | 204 | 1428 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4ORZH |  | 4,4,4 | 12Dr ORZH | 1 |  | Frozen Food | 12.168 | -7 | HG 2 Wire | 120 | 5.7 | 1.8 | 12.9 | 684 | 216 | 1548 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3ORZH |  | 5,4,3 | 12Dr ORZH | 1 |  | Frozen Food | 12.168 | -7 | HG 2 Wire | 120 | 5.7 | 1.9 | 13 | 684 | 228 | 1560 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2ORZH |  | 4,4,3,2 | 13Dr ORZH | 1 |  | Frozen Food | 13.182 | -7 | HG 2 Wire | 120 | 6.6 | 2 | 14.1 | 792 | 240 | 1692 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4ORZH |  | 5,4,4 | 13Dr ORZH | 1 |  | Frozen Food | 13.182 | -7 | HG 2 Wire | 120 | 6.1 | 2 | 14 | 732 | 240 | 1680 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3ORZH |  | 5,5,3 | 13Dr ORZH | 1 |  | Frozen Food | 13.182 | -7 | HG 2 Wire | 120 | 6.1 | 2.1 | 14.1 | 732 | 252 | 1692 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4ORZH |  | 5,5,4 | 14Dr ORZH | 1 |  | Frozen Food | 14.196 | -7 | HG 2 Wire | 120 | 6.5 | 2.2 | 15.1 | 780 | 264 | 1812 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,3,3ORZH |  | 4,4,3,3 | 14Dr ORZH | 1 |  | Frozen Food | 14.196 | -7 | HG 2 Wire | 120 | 6.8 | 2.2 | 15.2 | 816 | 264 | 1824 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,5ORZH |  | 5,5,5 | 15Dr ORZH | 1 |  | Frozen Food | 15.21 | -7 | HG 2 Wire | 120 | 6.9 | 2.4 | 16.2 | 828 | 288 | 1944 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,3ORZH |  | 4,4,4,3 | 15Dr ORZH | 1 |  | Frozen Food | 15.21 | -7 | HG 2 Wire | 120 | 7.2 | 2.3 | 16.2 | 864 | 276 | 1944 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,3,3ORZH |  | 5,5,3,3 | 16Dr ORZH | 1 |  | Frozen Food | 16.224 | -7 | HG 2 Wire | 120 | 7.6 | 2.6 | 17.4 | 912 | 312 | 2088 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,4,4ORZH |  | 4,4,4,4 | 16Dr ORZH | 1 |  | Frozen Food | 16.224 | -7 | HG 2 Wire | 120 | 7.6 | 2.4 | 17.2 | 912 | 288 | 2064 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
|  | ORZH-ELMD | Ice Cream | [7 empty] | Tnk htr amp | [6 empty] | 60
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
2ORZHIC |  | 2 | 2Dr ORZH | 1 |  | Ice Cream | 2.12 | -15 | HG 2 Wire | 120 | 1.3 | 0.3 | 2.2 | 156 | 36 | 264 | E14S250 |  | SORIT 12 |  |  | 5/8 | 1/2
3ORZHIC |  | 3 | 3Dr ORZH | 1 |  | Ice Cream | 3.18 | -15 | HG 2 Wire | 120 | 1.5 | 0.5 | 3.3 | 180 | 60 | 396 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
4ORZHIC |  | 4 | 4Dr ORZH | 1 |  | Ice Cream | 4.24 | -15 | HG 2 Wire | 120 | 1.9 | 0.6 | 4.3 | 228 | 72 | 516 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
5ORZHIC |  | 5 | 5Dr ORZH | 1 |  | Ice Cream | 5.3 | -15 | HG 2 Wire | 120 | 2.3 | 0.8 | 5.4 | 276 | 96 | 648 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
6ORZHIC |  | 6 | 6Dr ORZH | 1 |  | Ice Cream | 6.36 | -15 | HG 2 Wire | 120 | 2.7 | 1 | 6.4 | 324 | 120 | 768 | E14S250 |  | SORIT 12 |  |  | 7/8 | 5/8
3,3ORZHIC |  | 3,3 | 6Dr ORZH | 1 |  | Ice Cream | 6.36 | -15 | HG 2 Wire | 120 | 3 | 1 | 6.6 | 360 | 120 | 792 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,3ORZHIC |  | 4,3 | 7Dr ORZH | 1 |  | Ice Cream | 7.42 | -15 | HG 2 Wire | 120 | 3.4 | 1.1 | 7.6 | 408 | 132 | 912 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
4,4ORZHIC |  | 4,4 | 8Dr ORZH | 1 |  | Ice Cream | 8.48 | -15 | HG 2 Wire | 120 | 3.8 | 1.2 | 8.6 | 456 | 144 | 1032 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,3ORZHIC |  | 5,3 | 8Dr ORZH | 1 |  | Ice Cream | 8.48 | -15 | HG 2 Wire | 120 | 3.8 | 1.3 | 8.7 | 456 | 156 | 1044 | E14S250 |  | SORIT 12 |  |  | 1 1/8 | 5/8
5,4ORZHIC |  | 5,4 | 9Dr ORZH | 1 |  | Ice Cream | 9.54 | -15 | HG 2 Wire | 120 | 4.2 | 1.4 | 9.7 | 504 | 168 | 1164 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
3,3,3ORZHIC |  | 3,3,3 | 9Dr ORZH | 1 |  | Ice Cream | 9.54 | -15 | HG 2 Wire | 120 | 4.5 | 1.5 | 9.9 | 540 | 180 | 1188 | E14S250 |  | SORIT 12 |  |  | 1 3/8 | 5/8
5,5ORZHIC |  | 5,5 | 10Dr ORZH | 1 |  | Ice Cream | 10.6 | -15 | HG 2 Wire | 120 | 4.6 | 1.6 | 10.8 | 552 | 192 | 1296 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,3,3ORZHIC |  | 4,3,3 | 10Dr ORZH | 1 |  | Ice Cream | 10.6 | -15 | HG 2 Wire | 120 | 4.9 | 1.6 | 10.9 | 588 | 192 | 1308 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,3,3ORZHIC |  | 5,3,3 | 11Dr ORZH | 1 |  | Ice Cream | 11.66 | -15 | HG 2 Wire | 120 | 5.3 | 1.8 | 12 | 636 | 216 | 1440 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3ORZHIC |  | 4,4,3 | 11Dr ORZH | 1 |  | Ice Cream | 11.66 | -15 | HG 2 Wire | 120 | 5.3 | 1.7 | 11.9 | 636 | 204 | 1428 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,4ORZHIC |  | 4,4,4 | 12Dr ORZH | 1 |  | Ice Cream | 12.72 | -15 | HG 2 Wire | 120 | 5.7 | 1.8 | 12.9 | 684 | 216 | 1548 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,3ORZHIC |  | 5,4,3 | 12Dr ORZH | 1 |  | Ice Cream | 12.72 | -15 | HG 2 Wire | 120 | 5.7 | 1.9 | 13 | 684 | 228 | 1560 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
4,4,3,2ORZHIC |  | 4,4,3,2 | 13Dr ORZH | 1 |  | Ice Cream | 13.78 | -15 | HG 2 Wire | 120 | 6.6 | 2 | 14.1 | 792 | 240 | 1692 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,4,4ORZHIC |  | 5,4,4 | 13Dr ORZH | 1 |  | Ice Cream | 13.78 | -15 | HG 2 Wire | 120 | 6.1 | 2 | 14 | 732 | 240 | 1680 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,3ORZHIC |  | 5,5,3 | 13Dr ORZH | 1 |  | Ice Cream | 13.78 | -15 | HG 2 Wire | 120 | 6.1 | 2.1 | 14.1 | 732 | 252 | 1692 | E14S250 |  | SORIT 15 |  |  | 1 3/8 | 5/8
5,5,4ORZHIC |  | 5,5,4 | 14Dr ORZH | 1 |  | Ice Cream | 14.84 | -15 | HG 2 Wire | 120 | 6.5 | 2.2 | 15.1 | 780 | 264 | 1812 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
4,4,3,3ORZHIC |  | 4,4,3,3 | 14Dr ORZH | 1 |  | Ice Cream | 14.84 | -15 | HG 2 Wire | 120 | 6.8 | 2.2 | 15.2 | 816 | 264 | 1824 | E14S250 |  | SORIT 15 |  |  | 1 5/8 | 5/8
5,5,5ORZHIC |  | 5,5,5 | 15Dr ORZH | 1 |  | Ice Cream | 15.9 | -15 | HG 2 Wire | 120 | 6.9 | 2.4 | 16.2 | 828 | 288 | 1944 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,3ORZHIC |  | 4,4,4,3 | 15Dr ORZH | 1 |  | Ice Cream | 15.9 | -15 | HG 2 Wire | 120 | 7.2 | 2.3 | 16.2 | 864 | 276 | 1944 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
5,5,3,3ORZHIC |  | 5,5,3,3 | 16Dr ORZH | 1 |  | Ice Cream | 16.96 | -15 | HG 2 Wire | 120 | 7.6 | 2.6 | 17.4 | 912 | 312 | 2088 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
4,4,4,4ORZHIC |  | 4,4,4,4 | 16Dr ORZH | 1 |  | Ice Cream | 16.96 | -15 | HG 2 Wire | 120 | 7.6 | 2.4 | 17.2 | 912 | 288 | 2064 | E14S250 |  | SORIT 20 |  |  | 1 5/8 | 5/8
|  |  |  | TEMP | EXPAN |  |  | EVAP | TYPE OF |  | FAN | LIGHT | A/S | FAN | LIGHT | A/S |  | DEGREE |  | RUN LG | SUCTION |  | LIQUID
ENTER THIS |  | SIZE | MODEL | PROBE | VALVE | APPLIC | MBH | ° F | DEFROST | VOLTS | AMPS | AMPS | AMPS | WATTS | WATTS | WATTS | HOTGAS | LIQUID | SUCTION | IN FEET | HORIZON | RISER | LINE
10PTDG |  | 10' | 10' PTDG | 1 |  | Service Seafood | 10 | 15 | Off Cycle | 120 | 1.72 | 3 | 120 | 206.4 | 360 | 14400 |  |  | SORIT 12
[14 empty] | 0 | 0 | 0
10DB |  | 10' | 10' DB | 1 |  | Deli Backbar | 13.1 | 26 | Off Cycle | 120 | 1.2 | 1.2 |  | 144 | 144 | 0 |  |  | SORIT 12
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0

## Compressor rla
1 | 2 | 3 | 4 | 5 | 6 | 7
Compressor | 208v | 460v | HP | UNLD
06DA537 | 63.6 | 28.6 | 15
06DA818 | 31.4 | 15.7 | 6.5
06DA824 | 39.6 | 19.8 | 7.5
06DM313 | 19.3 | 9.6 | 5
06DM316 | 19.3 | 9.6 | 5
06DM337 | 44.3 | 22.1 | 10
06DM808 | 12.4 | 6.2 | 3
06DR109 | 8.6 | 3.9 | 2
06DR228 | 39.6 | 19.8 | 7.5
06DR316 | 19.3 | 9.6 | 5
06DR337 | 44.3 | 22.1 | 10
06DR718 | 19.3 | 9.6 | 5
06DR724 | 31.4 | 15.7 | 6.5
06DR820 | 31.4 | 15.7 | 6.5
06EA250 | 74.3 | 35 | 20
06EA265 | 90.7 | 45.7 | 25
06EA275 | 116.4 | 52.1 | 30
06EA299 | 153.6 | 75.7 | 40
06EM150 | 64.3 | 33.9 | 15
06EM450 | 64.3 | 33.9 | 15
06EM750 | 64.3 | 33.9 | 15 | 50%
06EZ150 | 64.3 | 33.9 | 15
06EZ450 | 64.3 | 33.9 | 15
06EZ750 | 64.3 | 33.9 | 15 | 50%
06EM175 | 90.7 | 45.7 | 25
06EM475 | 90.7 | 45.7 | 25
06EM775 | 90.7 | 45.7 | 25 | 33%
06EZ175 | 90.7 | 45.7 | 25
06EZ475 | 90.7 | 45.7 | 25
06EZ775 | 90.7 | 45.7 | 25 | 33%
06EM199 | 130 | 62.9 | 35
06EM499 | 130 | 62.9 | 35
06EM799 | 130 | 62.9 | 35 | 33%
06EZ199 | 130 | 62.9 | 35
06EZ499 | 130 | 62.9 | 35
06EZ799 | 130 | 62.9 | 35 | 33%
06ER099 | 116.4 | 52.1 | 30
06ER399 | 116.4 | 52.1 | 30
06ER799 | 116.4 | 52.1 | 30 | 33%
06EY099 | 116.4 | 52.1 | 30
06EY399 | 116.4 | 52.1 | 30
06EY799 | 116.4 | 52.1 | 30 | 33%
06ER150 | 59.3 | 33.9 | 15
06ER450 | 59.3 | 33.9 | 15
06ER750 | 59.3 | 33.9 | 15 | 50%
06EY150 | 59.3 | 33.9 | 15
06EY450 | 59.3 | 33.9 | 15
06EY750 | 59.3 | 33.9 | 15 | 50%
06ER165 | 74.3 | 35 | 20
06ER465 | 74.3 | 35 | 20
06ER765 | 74.3 | 35 | 20 | 33%
06EY165 | 74.3 | 35 | 20
06EY465 | 74.3 | 35 | 20
06EY765 | 74.3 | 35 | 20 | 33%
06ER175 | 74.3 | 35 | 20
06ER475 | 74.3 | 35 | 20
06ER775 | 74.3 | 35 | 20 | 33%
06EY175 | 74.3 | 35 | 20
06EY475 | 74.3 | 35 | 20
06EY775 | 74.3 | 35 | 20 | 33%
2DA0600 | 28.8 | 10.2 | 6 |  | 2DA3F23KL-TFC
2DA0750 | 32 | 14.1 | 7.5 |  | 2DA3R89KL-TFC
2DB0500 | 19.2 | 10.2 | 5 |  | 2DB3R61KL-TFC
2DB0600 | 28.2 | 13.3 | 6 |  | 2DB3F25KL-TFC
2DC0500 | 22.3 | 10.4 | 5 |  | 2DC3R53KL-TFC
2DD0500 | 22.3 | 10.5 | 5 |  | 2DD3R63KL-TFC
2DF0300 | 16.8 | 8.1 | 3 |  | 2DF3F16KL-TFC
2DL0400 | 26.3 | 10.2 | 4 |  | 2DL3F20KL-TFC
2DL0750 | 31.6 | 13.8 | 7.5 |  | 2DL3R78KL-TFC
3DA0600 | 30.3 | 16.8 | 6 |  | 3DA3F28KL-TFC
3DA0750 | 41 | 20 | 7.5 |  | 3DA3R10ML-TFC
3DB0750 | 31.5 | 16.1 | 7.5 |  | 3DB3F33KL-TFC
3DB1000 | 43.6 | 20 | 10 |  | 3DB3R12ML-TFC
3DF0900 | 39 | 16.9 | 9 |  | 3DF3F40KL-TFC
3DF1200 | 48.2 | 23.6 | 12 |  | 3DF3R15ML-TFC
3DF4S11ML | 42.6 | 21.3 | 10 |  | 3DF4S11ML-TFC
3DH0600 | 30.3 | 16.8 | 6 | UNLD
3DK1200 | 48.2 | 23.6 | 12 | UNLD
3DP1000 | 43.6 | 20 | 10 | UNLD | 3DP3R12ML-TFC
3DS1000 | 42 | 18.6 | 10 |  | 3DS3F46KL-TFC
3DS1500 | 59.6 | 29 | 15 |  | 3DS3R17ML-TFC
3DS4S12ML | 47.1 | 23.5 | 10 |  | 3DS4S12ML-TFC
3DT1500 | 59.6 | 29 | 15 | UNLD | 3DT3R17ML-TFC
4DA1010 | 45.2 | 21 | 10 |  | 4DA3F47KL-TSK
4DA2000 | 66 | 33 | 20 |  | 4DA3R18ML-TSK
4DE2000 | 66 | 33 | 20 | UNLD | 4DE3R18ML-TSK
4DH2500 | 82.2 | 41.1 | 25 |  | 4DH3R22ML-TSK
4DJ3000 | 94 | 47 | 30 |  | 4DJ3R28ML-TSK
4DK2500 | 82.2 | 41.1 | 25 | UNLD | 4DK3R22ML-TSK
4DH1500 | 52.6 | 26.3 | 10 |  | 4DH3F63KL-TSK |  | no oil cooler
4DL1500 | 52.6 | 26.3 | 15 |  | 4DL3F63KL-TSK
4DN1010 | 45.2 | 23 | 10 | UNLD
4DP1500 | 52.6 | 26.3 | 15 | UNLD | 4DP3F63KL-TSK
4DS2200 | 66 | 33 | 22 | UNLD | 4DS3F76KL-TSK
4DJ2200 | 56.6 | 33 | 12.5 |  | 4DJ3F76KL-TSK |  | no oil cooler
4DT2200 | 66 | 33 | 22 |  | 4DT3F76KL-TSK
6DL2700 | 80.8 | 40.4 | 27 |  | 6DL3F93KL-TSK
2DA3F23KL-TFC | 28.8 | 10.2 | 6
2DA3R89KL-TFC | 32 | 14.1 | 7.5
2DB3R61KL-TFC | 19.2 | 10.2 | 5
2DB3F25KL-TFC | 28.2 | 13.3 | 6
2DC3R53KL-TFC | 22.3 | 10.4 | 5
2DD3R63KL-TFC | 22.3 | 10.5 | 5
2DF3F16KL-TFC | 16.8 | 8.1 | 3
2DL3F20KL-TFC | 26.3 | 10.2 | 4
2DL3R78KL-TFC | 31.6 | 13.8 | 7.5
3DA3F28KL-TFC | 30.3 | 16.8 | 6
3DA3R10ML-TFC | 41 | 20 | 7.5
3DB3F33KL-TFC | 31.5 | 16.1 | 7.5
3DB3R12ML-TFC | 43.6 | 20 | 10
3DF3F40KL-TFC | 39 | 16.9 | 9
3DF3R15ML-TFC | 48.2 | 23.6 | 12
3DF4S11ML-TFC | 42.6 | 21.3 | 10
3DP3R12ML-TFC | 43.6 | 20 | 10 | UNLD
3DS3F46KL-TFC | 42 | 18.6 | 10
3DS3R17ML-TFC | 59.6 | 29 | 15
3DS4S12ML-TFC | 47.1 | 23.5 | 10
3DT3R17ML-TFC | 59.6 | 29 | 15 | UNLD
4DA3F47KL-TSK | 45.2 | 21 | 10 |  |  |  | discontinued 2012
4DA3R18ML-TSK | 66 | 33 | 20 |  |  |  | discontinued 2012
4DE3R18ML-TSK | 66 | 33 | 20 | UNLD |  |  | discontinued 2012
4DH3S16ML-TSK | 65.7 | 32.9 | 15 |  |  |  |  | discontinued 2012
4DH3R22ML-TSK | 82.2 | 41.1 | 25 |  |  |  |  | discontinued 2012
4DJ3R28ML-TSK | 94 | 47 | 30 |  |  |  |  | discontinued 2012
4DK3R22ML-TSK | 82.2 | 41.1 | 25 | UNLD |  |  |  | discontinued 2012
4DH3F63KL-TSK | 52.6 | 26.3 | 10 |  |  |  | no oil cooler | discontinued 2012
4DL3F63KL-TSK | 52.6 | 26.3 | 15 |  |  |  |  | discontinued 2012
4DP3F63KL-TSK | 52.6 | 26.3 | 15 | UNLD |  |  |  | discontinued 2012
4DS3F76KL-TSK | 66 | 33 | 22 | UNLD |  |  |  | discontinued 2012
4DJ3F76KL-TSK | 56.6 | 33 | 12.5 |  |  |  | no oil cooler | discontinued 2012
4DT3F76KL-TSK | 66 | 33 | 22 |  |  |  |  | discontinued 2012
4DBNR20ML-TSK | 65.6 | 32.8 | 13.5 |  |  |  | introduced in 2012
4DCNR20ML-TSK | 65.6 | 32.8 | 13.5 | UNLD |  |  | introduced in 2012
4DHNR22ML-TSK | 82.1 | 41.1 | 15 |  |  |  | introduced in 2012
4DKNR22ML-TSK | 82.1 | 41.1 | 15 | UNLD |  |  | introduced in 2012
4DJNR28ML-TSK | 94 | 47 | 18 |  |  |  | introduced in 2012
4DRNR28ML-TSK | 94 | 47 | 18 | UNLD |  |  | introduced in 2012

## MCA MOPD CALC
MCA & MOPD CALC | [14 empty] | 230/1 EVAP AMPERAGE CALC | [6 empty] | BREAKERS
| RACK A |  | RACK B |  | RACK A |  | RACK B |  | RACK C |  | RACK D |  |  | a | a | b | a | b | c |  | d
| SHT 2 | RLA | SHT 3 | RLA | SHT 4 | RLA | SHT 5 | RLA | SHT 6 | RLA | SHT 7 | RLA |  | SHT 1 | SHT 2 | SHT 3 | SHT 4 | SHT 5 | SHT 6 | SHT 7 | SHT 8 | 100 | 100 | 110
1 | 2DA3R89KL-TFC | 32 | 2DL3F20KL-TFC | 31.6 | 0 |  | 0 |  | 0 |  | 0 |  | 1 |  |  | 5 | [5 empty] | 110 | 110 | 125
2 | 2DA3R89KL-TFC | 32 | 3DB3F33KL-TFC | 43.6 | 0 |  | 0 |  | 0 |  | 0 |  | 2 |  |  | 9.6 | [5 empty] | 125 | 125 | 150
3 | 3DB3R12ML-TFC | 43.6 | 3DS3F46KL-TFC | 59.6 | 0 |  | 0 |  | 0 |  | 0 |  | 3 | [8 empty] | 150 | 150 | 175
4 | 3DS3R17ML-TFC | 59.6 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 4 | [8 empty] | 175 | 175 | 200
5 | 4DH3R22ML-TSK | 82.2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 5 |  | 0 | [6 empty] | 200 | 200 | 225
6 | 4DH3R22ML-TSK | 82.2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6 |  | 0 | [6 empty] | 225 | 225
7 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 7
8 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 8 |  |  | 2 | [7 empty] | 250
9 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 9 | [8 empty] | 250 | 250 | 300
10 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 10 |  |  | #N/A | [5 empty] | 300 | 300 | 350
| EVAP FAN | 0 | EVAP FAN | #N/A | EVAP FAN | 0 | EVAP FAN | 0 | EVAP FAN | 0 | EVAP FAN | 0 | 11 | [8 empty] | 350 | 350 | 400
| CONTROL | 8 | CONTROL | 8 | CONTROL | 8 | CONTROL | 8 | CONTROL | 8 | CONTROL | 8 | 12 | [8 empty] | 400 | 400 | 450
|  | 0 | [10 empty] | 13 | [8 empty] | 450 | 450 | 500
| COND |  | COND |  | COND |  | COND |  | COND |  | COND |  | 14 | [8 empty] | 500 | 500 | 600
[13 empty] | 15 | [8 empty] | 600 | 600 | 700
| FLA | 339.6 | FLA | #N/A | FLA | 8 | FLA | 8 | FLA | 8 | FLA | 8 | 16 | [8 empty] | 700 | 700 | 800
| MAX | 82.2 | MAX | #N/A | MAX | 8 | MAX | 8 | MAX | 8 | MAX | 8 | 17 | [8 empty] | 800 | 800 | 900
| MCA | 360.15 | MCA | #N/A | MCA | 10 | MCA | 10 | MCA | 10 | MCA | 10 | 18
| MOPD | 442.35 | MOPD | #N/A | MOPD | 18 | MOPD | 18 | MOPD | 18 | MOPD | 18 | 19
| BREAKER | 400 | BREAKER | #N/A | BREAKER | #N/A | BREAKER | #N/A | BREAKER | #N/A | BREAKER | #N/A | 20
| Lookup | 400 | Lookup | #N/A | Lookup | #N/A | Lookup | #N/A | Lookup | #N/A | Lookup | #N/A | 19
| Max Brkr | 400 | Max Brkr | #N/A | Max Brkr | #N/A | Max Brkr | #N/A | Max Brkr | #N/A | Max Brkr | #N/A | 20
21
[13 empty] | TOTAL | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0

## Breaker Contactor
Ampacity | Cir/Bkr | Wire |  | Amps | Contactor
1 | 2 | 3 | 4 | 5 | 6
6 | 15A | #12 |  | 5 | 25A
9 | 15A | #12 |  | 11 | 25A
13 | 20A | #12 |  | 16 | 25A
15 | 30A | #10 |  | 23 | 30A
25 | 40A | #8 |  | 30 | 40A
33 | 50A | #8 |  | 40 | 50A
41 | 60A | #6 |  | 50 | 60A
47.5 | 70A | #4 |  | 60 | 75A
55 | 80A | #4 |  | 75 | 90A
65.5 | 90A | #3 |  | 90 | 120A
73 | 100A | #3 |  | 125
80 | 125A | #1
84 | 125A | #1

## UPDATED Condenser_Look
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
MODEL | SIZE | FPI | FANS | WEIGHT | FLA | MCA | MOPD | R22 | R507 | VOLTAGE
KAC 22 | 48"x98" | 10 | 1x2 | 465 | 12.8 | 14.4 | 25 | 12.6 | 12.348 | 208/60/3
KAC 25 | 48"x98" | 10 | 1x2 | 495 | 12.8 | 14.4 | 25 | 12.6 | 12.348 | 208/60/3
KAC 29 | 48"x98" | 10 | 1x2 | 520 | 12.8 | 14.4 | 25 | 12.6 | 12.348 | 208/60/3
KAC 31 | 48"x98" | 10 | 1x2 | 550 | 12.8 | 14.4 | 25 | 15.2 | 14.896 | 208/60/3
KAC 35 | 48"x98" | 10 | 1x2 | 600 | 12.8 | 14.4 | 25 | 16.9 | 16.562 | 208/60/3
KAC 42 | 48"x146" | 10 | 1x3 | 800 | 19.2 | 20.8 | 30 | 18.9 | 18.522 | 208/60/3
KAC 48 | 48"x146" | 10 | 1x3 | 900 | 19.2 | 20.8 | 30 | 22.9 | 22.442 | 208/60/3
KAC 55 | 48"x146" | 10 | 1x3 | 1000 | 19.2 | 20.8 | 30 | 25.4 | 24.892 | 208/60/3
KAC 58 | 48"x194" | 10 | 1x4 | 1050 | 25.6 | 27.2 | 40 | 25.2 | 24.696 | 208/60/3
KAC 62 | 48"x194" | 10 | 1x4 | 1100 | 25.6 | 27.2 | 40 | 30.5 | 29.89 | 208/60/3
KAC 67 | 48"x194" | 10 | 1x4 | 1150 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
KAC 72 | 48"x194" | 10 | 1x4 | 1200 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
KAC 59 | 96"x98" | 10 | 2x2 | 1080 | 25.6 | 27.2 | 40 | 25.2 | 24.696 | 208/60/3
KAC 63 | 96"x98" | 10 | 2x2 | 1140 | 25.6 | 27.2 | 40 | 30.5 | 29.89 | 208/60/3
KAC 68 | 96"x98" | 10 | 2x2 | 1190 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
KAC 73 | 96"x98" | 10 | 2x2 | 1240 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
KAC 83 | 96"x146" | 10 | 2x3 | 1640 | 38.4 | 40 | 50 | 37.8 | 37.044 | 208/60/3
KAC 95 | 96"x146" | 10 | 2x3 | 1840 | 38.4 | 40 | 50 | 46.7 | 45.766 | 208/60/3
KAC 102 | 96"x146" | 10 | 2x3 | 2050 | 38.4 | 40 | 50 | 50.7 | 49.686 | 208/60/3
KAC 116 | 96"x194" | 10 | 2x4 | 2150 | 51.2 | 52.8 | 70 | 50.4 | 49.392 | 208/60/3
KAC 127 | 96"x194" | 10 | 2x4 | 2250 | 51.2 | 52.8 | 70 | 60.9 | 59.682 | 208/60/3
KAC 134 | 96"x194" | 10 | 2x4 | 2350 | 51.2 | 52.8 | 70 | 67.7 | 66.346 | 208/60/3
KAC 144 | 96"x194" | 10 | 2x4 | 2460 | 51.2 | 52.8 | 70 | 67.7 | 66.346 | 208/60/3
KAC 158 | 96"x242" | 10 | 2x5 | 2800 | 64 | 65.6 | 80 | 76.1 | 74.578 | 208/60/3
KAC 168 | 96"x242" | 10 | 2x5 | 2950 | 64 | 65.6 | 80 | 84.5 | 82.81 | 208/60/3
KAC 180 | 96"x242" | 10 | 2x5 | 3075 | 64 | 65.6 | 80 | 84.6 | 82.908 | 208/60/3
KAC 190 | 96"x290" | 10 | 2x6 | 3400 | 76.8 | 78.4 | 100 | 91.4 | 89.572 | 208/60/3
KAC 202 | 96"x290" | 10 | 2x6 | 3620 | 76.8 | 78.4 | 100 | 101.4 | 99.372 | 208/60/3
KAC 216 | 96"x290" | 10 | 2x6 | 3750 | 76.8 | 78.4 | 100 | 101.5 | 99.47 | 208/60/3
4)CC3-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 32.31 | 31.6638 | 208/60/3
4)CC4-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 37.55 | 36.799 | 208/60/3
4)CC5-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 41.17 | 40.3466 | 208/60/3
4)CC6-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 43.38 | 42.5124 | 208/60/3
4)CC3-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 40.62 | 39.8076 | 208/60/3
4)CC4-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 47.3 | 46.354 | 208/60/3
4)CC5-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 52.32 | 51.2736 | 208/60/3
4)CC6-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 55.11 | 54.0078 | 208/60/3
2)CC4-35-180 |  | 10 | 6 |  | 33.6 | 35 | 50 | 35.32 | 34.6136 | 208/60/3
2)CC4-35-90 |  | 10 | 3 |  | 16.8 | 18.2 | 30 | 17.64 | 17.2872 | 208/60/3
2)CC4-35-120 |  | 10 | 4 |  | 22.4 | 23.8 | 30 | 23.56 | 23.0888 | 208/60/3
2)CC4-35-150 |  | 10 | 5 |  | 28 | 29.4 | 40 | 29.44 | 28.8512 | 208/60/3
2)CC4-35-180 |  | 10 | 6 |  | 33.6 | 35 | 50 | 35.32 | 34.6136 | 208/60/3
4)CC4-35-90 |  | 10 | 6 |  | 33.6 | 35 | 50 | 35.28 | 34.5744 | 208/60/3
4)CC4-35-120 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 47.12 | 46.1776 | 208/60/3
4)CC4-35-150 |  | 10 | 10 |  | 56 | 57.4 | 70 | 58.88 | 57.7024 | 208/60/3
4)CC4-35-180 |  | 10 | 12 |  | 67.2 | 68.6 | 90 | 70.64 | 69.2272 | 208/60/3
2)CC5-35-150 |  | 10 | 5 |  | 28 | 29.4 | 40 | 32.19 | 31.5462 | 208/60/3
4)CC5-35-150 |  | 10 | 10 |  | 56 | 57.4 | 70 | 64.37 | 63.0826 | 208/60/3
VAC 22 | 48"x98" | 10 | 1x2 | 465 | 12.8 | 14.4 | 25 | 12.6 | 12.348 | 208/60/3
VAC 25 | 48"x98" | 10 | 1x2 | 495 | 12.8 | 14.4 | 25 | 12.6 | 12.348 | 208/60/3
VAC 29 | 48"x98" | 10 | 1x2 | 520 | 12.8 | 14.4 | 25 | 12.6 | 12.348 | 208/60/3
VAC 31 | 48"x98" | 10 | 1x2 | 550 | 12.8 | 14.4 | 25 | 15.2 | 14.896 | 208/60/3
VAC 35 | 48"x98" | 10 | 1x2 | 600 | 12.8 | 14.4 | 25 | 16.9 | 16.562 | 208/60/3
VAC 42 | 48"x146" | 10 | 1x3 | 800 | 19.2 | 20.8 | 30 | 18.9 | 18.522 | 208/60/3
VAC 48 | 48"x146" | 10 | 1x3 | 900 | 19.2 | 20.8 | 30 | 22.9 | 22.442 | 208/60/3
VAC 55 | 48"x146" | 10 | 1x3 | 1000 | 19.2 | 20.8 | 30 | 25.4 | 24.892 | 208/60/3
VAC 58 | 48"x194" | 10 | 1x4 | 1050 | 25.6 | 27.2 | 40 | 25.2 | 24.696 | 208/60/3
VAC 62 | 48"x194" | 10 | 1x4 | 1100 | 25.6 | 27.2 | 40 | 30.5 | 29.89 | 208/60/3
VAC 67 | 48"x194" | 10 | 1x4 | 1150 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
VAC 72 | 48"x194" | 10 | 1x4 | 1200 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
VAC 59 | 96"x98" | 10 | 2x2 | 1080 | 25.6 | 27.2 | 40 | 25.2 | 24.696 | 208/60/3
VAC 63 | 96"x98" | 10 | 2x2 | 1140 | 25.6 | 27.2 | 40 | 30.5 | 29.89 | 208/60/3
VAC 68 | 96"x98" | 10 | 2x2 | 1190 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
VAC 73 | 96"x98" | 10 | 2x2 | 1240 | 25.6 | 27.2 | 40 | 33.8 | 33.124 | 208/60/3
VAC 83 | 96"x146" | 10 | 2x3 | 1640 | 38.4 | 40 | 50 | 37.8 | 37.044 | 208/60/3
VAC 95 | 96"x146" | 10 | 2x3 | 1840 | 38.4 | 40 | 50 | 46.7 | 45.766 | 208/60/3
VAC 102 | 96"x146" | 10 | 2x3 | 2050 | 38.4 | 40 | 50 | 50.7 | 49.686 | 208/60/3
VAC 116 | 96"x194" | 10 | 2x4 | 2150 | 51.2 | 52.8 | 70 | 50.4 | 49.392 | 208/60/3
VAC 127 | 96"x194" | 10 | 2x4 | 2250 | 51.2 | 52.8 | 70 | 60.9 | 59.682 | 208/60/3
VAC 134 | 96"x194" | 10 | 2x4 | 2350 | 51.2 | 52.8 | 70 | 67.7 | 66.346 | 208/60/3
VAC 144 | 96"x194" | 10 | 2x4 | 2460 | 51.2 | 52.8 | 70 | 67.7 | 66.346 | 208/60/3
VAC 158 | 96"x242" | 10 | 2x5 | 2800 | 64 | 65.6 | 80 | 76.1 | 74.578 | 208/60/3
VAC 168 | 96"x242" | 10 | 2x5 | 2950 | 64 | 65.6 | 80 | 84.5 | 82.81 | 208/60/3
VAC 180 | 96"x242" | 10 | 2x5 | 3075 | 64 | 65.6 | 80 | 84.6 | 82.908 | 208/60/3
VAC 190 | 96"x290" | 10 | 2x6 | 3400 | 76.8 | 78.4 | 100 | 91.4 | 89.572 | 208/60/3
VAC 202 | 96"x290" | 10 | 2x6 | 3620 | 76.8 | 78.4 | 100 | 101.4 | 99.372 | 208/60/3
VAC 216 | 96"x290" | 10 | 2x6 | 3750 | 76.8 | 78.4 | 100 | 101.5 | 99.47 | 208/60/3
ACE 034FB | 96"x98" | 10 | 2x2 | 1200 | 11.2 | 15 | 15 | 15.3 | 14.994 | 208/60/3
ACE 038FB | 96"x98" | 10 | 2x2 | 1250 | 11.2 | 15 | 15 | 19.6 | 19.208 | 208/60/3
ACE 044FB | 96"x98" | 10 | 2x2 | 1420 | 11.2 | 15 | 15 | 21.6 | 21.168 | 208/60/3
ACE 051FB | 96"x146" | 10 | 2x3 | 1740 | 16.8 | 17.5 | 20 | 24 | 23.52 | 208/60/3
ACE 056FB | 96"x146" | 10 | 2x3 | 1830 | 16.8 | 17.5 | 20 | 29.5 | 28.91 | 208/60/3
ACE 065FB | 96"x146" | 10 | 2x3 | 2050 | 16.8 | 17.5 | 20 | 32.3 | 31.654 | 208/60/3
ACE 075FB | 96"x194" | 10 | 2x4 | 2420 | 22.4 | 23.1 | 25 | 39.1 | 38.318 | 208/60/3
ACE 086FB | 96"x194" | 10 | 2x4 | 2770 | 22.4 | 23.1 | 25 | 43.5 | 42.63 | 208/60/3
ACE 100FB | 96"x242" | 10 | 2x5 | 3280 | 28 | 28.7 | 30 | 50.1 | 49.098 | 208/60/3
2) ACE 100FB | 96"x242" | 10 | 2x5 | 3280 | 28 | 28.7 | 30 | 100.2 | 98.2 | 208/60/3
ACE 105FB | 96"x242" | 10 | 2x5 | 3410 | 28 | 28.7 | 30 | 55 | 53.9 | 208/60/3
ACE 126FB | 96"x290" | 10 | 2x6 | 4090 | 33.6 | 34.3 | 35 | 69.4 | 68.012 | 208/60/3
ACE 147FB | 96"x338" | 10 | 2x7 | 4771 | 39.2 | 39.9 | 40 | 80.6 | 78.988 | 208/60/3
ACE 152FB | 96"x338" | 10 | 2x7 | 4771 | 39.2 | 39.9 | 40 | 81.6 | 79.968 | 208/60/3
R404A
BNQ-D04-A016 | 88"x112" | 10 | 2x2 | 1288 | 14 | 15 | 20 | 16 | 15.6 | 208/60/3
BNQ-D04-A021 | 88"x112" | 10 | 2x2 | 1410 | 14 | 15 | 20 | 20.7 | 20.3 | 208/60/3
BNQ-D04-A023 | 88"x112" | 10 | 2x2 | 1532 | 14 | 15 | 20 | 22.9 | 22.4 | 208/60/3
BNQ-D06-A031 | 88"x165" | 10 | 2x3 | 2086 | 21 | 21.9 | 30 | 31 | 30.4 | 208/60/3
BNQ-D06-A034 | 88"x165" | 10 | 2x3 | 2268 | 21 | 21.9 | 30 | 34.4 | 33.7 | 208/60/3
BNQ-D08-A041 | 88"x218" | 10 | 2x4 | 2838 | 28 | 28.9 | 35 | 41.4 | 40.6 | 208/60/3
BNQ-D08-A046 | 88"x218" | 10 | 2x4 | 3106 | 28 | 28.9 | 35 | 45.8 | 44.9 | 208/60/3
BNQ-D10-A052 | 88"x271" | 10 | 2x5 | 3530 | 35 | 35.9 | 45 | 51.8 | 50.7 | 208/60/3
BNQ-D10-A057 | 88"x271" | 10 | 2x5 | 3861 | 35 | 35.9 | 45 | 57.3 | 56.1 | 208/60/3
BNQ-D12-A069 | 88"x324" | 10 | 2x6 | 4552 | 42 | 42.9 | 50 | 68.7 | 67.3 | 208/60/3
BNQ-D14-A083 | 88"x377" | 10 | 2x7 | 5125 | 49 | 49.9 | 50 | 83.1 | 81.5 | 208/60/3
VEQ 21 | 48"x98" | 10 | 1x2 | 465 | 10.6 | 11.9 | 15 | 10.29 |  | 208/60/3
VEQ 23 | 48"x98" | 10 | 1x2 | 495 | 10.6 | 11.9 | 15 | 11.02 |  | 208/60/3
VEQ 24 | 48"x98" | 10 | 1x2 | 520 | 10.6 | 11.9 | 15 | 10.99 |  | 208/60/3
VEQ 27 | 48"x98" | 10 | 1x2 | 550 | 10.6 | 11.9 | 15 | 13.32 |  | 208/60/3
VEQ 32 | 48"x98" | 10 | 1x2 | 600 | 10.6 | 11.9 | 15 | 14.37 |  | 208/60/3
VEQ 36 | 48"x146" | 10 | 1x3 | 800 | 15.9 | 17.3 | 25 | 16.48 |  | 208/60/3
VEQ 40 | 48"x146" | 10 | 1x3 | 900 | 15.9 | 17.3 | 25 | 20.03 |  | 208/60/3
VEQ 45 | 48"x146" | 10 | 1x3 | 1000 | 15.9 | 17.3 | 25 | 22.24 |  | 208/60/3
VEQ 49 | 48"x194" | 10 | 1x4 | 1050 | 21.2 | 22.5 | 30 | 21.97 |  | 208/60/3
VEQ 54 | 48"x194" | 10 | 1x4 | 1100 | 21.2 | 22.5 | 30 | 26.65 |  | 208/60/3
VEQ 60 | 48"x194" | 10 | 1x4 | 1150 | 21.2 | 22.5 | 30 | 29.59 |  | 208/60/3
VEQ 64 | 48"x194" | 10 | 1x4 | 1200 | 21.2 | 22.5 | 30 | 28.74 |  | 208/60/3
VEQ 69 | 48"x242" | 10 | 1x5 | 1370 | 26.5 | 27.8 | 40 | 33.31 |  | 208/60/3
VEQ 75 | 48"x242" | 10 | 1x5 | 1430 | 26.5 | 27.8 | 40 | 36.96 |  | 208/60/3
VEQ 80 | 48"x242" | 10 | 1x5 | 1490 | 26.5 | 27.8 | 40 | 35.92 |  | 208/60/3
VEQ 81 | 48"x290" | 10 | 1x6 | 1690 | 31.8 | 33.2 | 40 | 39.97 |  | 208/60/3
VEQ 89 | 48"x290" | 10 | 1x6 | 1750 | 31.8 | 33.2 | 40 | 44.36 |  | 208/60/3
VEQ 94 | 48"x290" | 10 | 1x6 | 1830 | 31.8 | 33.2 | 40 | 43.11 |  | 208/60/3
VEQ 50 | 96"x98" | 10 | 2x2 | 1080 | 21.2 | 22.5 | 30 | 22.5 |  | 208/60/3
VEQ 56 | 96"x98" | 10 | 2x2 | 1140 | 21.2 | 22.5 | 30 | 26.65 |  | 208/60/3
VEQ 61 | 96"x98" | 10 | 2x2 | 1190 | 21.2 | 22.5 | 30 | 29.59 |  | 208/60/3
VEQ 65 | 96"x98" | 10 | 2x2 | 1240 | 21.2 | 22.5 | 30 | 29.5 |  | 208/60/3
VEQ 74 | 96"x146" | 10 | 2x3 | 1640 | 31.8 | 33.2 | 40 | 33.8 |  | 208/60/3
VEQ 82 | 96"x146" | 10 | 2x3 | 1840 | 31.8 | 33.2 | 40 | 40.89 |  | 208/60/3
VEQ 91 | 96"x146" | 10 | 2x3 | 2050 | 31.8 | 33.2 | 40 | 44.38 |  | 208/60/3
VEQ 97 | 96"x194" | 10 | 2x4 | 2150 | 42.4 | 43.7 | 60 | 45.1 |  | 208/60/3
VEQ 107 | 96"x194" | 10 | 2x4 | 2250 | 42.4 | 43.7 | 60 | 53 |  | 208/60/3
VEQ 119 | 96"x194" | 10 | 2x4 | 2350 | 42.4 | 43.7 | 60 | 59.19 |  | 208/60/3
VEQ 126 | 96"x194" | 10 | 2x4 | 2460 | 42.4 | 43.7 | 60 | 59 |  | 208/60/3
VEQ 135 | 96"x242" | 10 | 2x5 | 2800 | 53 | 54.3 | 70 | 66.61 |  | 208/60/3
VEQ 149 | 96"x242" | 10 | 2x5 | 2950 | 53 | 54.3 | 70 | 73.93 |  | 208/60/3
VEQ 157 | 96"x242" | 10 | 2x5 | 3075 | 53 | 54.3 | 70 | 73.7 |  | 208/60/3
VEQ 161 | 96"x290" | 10 | 2x6 | 3400 | 63.6 | 65 | 80 | 79.93 |  | 208/60/3
VEQ 179 | 96"x290" | 10 | 2x6 | 3620 | 63.6 | 65 | 80 | 88.71 |  | 208/60/3
VEQ 189 | 96"x290" | 10 | 2x6 | 3750 | 63.6 | 65 | 80 | 88.5 |  | 208/60/3
RDS 008 | 48.5"x52.5.5" | 10 | 1x1 | 320 | 2.8 | 15 | 15 | 4 | 4.1 | 208/60/3
RDS 010 | 48.5"x52.5.5" | 10 | 1x1 | 350 | 2.8 | 15 | 15 | 5.4 | 5.3 | 208/60/3
RDS 011 | 48.5"x52.5.5" | 10 | 1x1 | 380 | 2.8 | 15 | 15 | 6.2 | 5.8 | 208/60/3
RDS 015 | 48.5"x100.5" | 10 | 1x2 | 590 | 5.6 | 15 | 15 | 8.1 | 8.2 | 208/60/3
RDS 019 | 48.5"x100.5" | 10 | 1x2 | 640 | 5.6 | 15 | 15 | 10.7 | 10.5 | 208/60/3
RDS 021 | 48.5"x100.5" | 10 | 1x2 | 700 | 5.6 | 15 | 15 | 12.3 | 11.5 | 208/60/3
RDS 029 | 48.5x148.5" | 10 | 1x3 | 930 | 8.4 | 15 | 15 | 16.2 | 15.8 | 208/60/3
RDS 032 | 48.5x148.5" | 10 | 1x3 | 1000 | 8.4 | 15 | 15 | 18.4 | 17.3 | 208/60/3
RDS 039 | 48.5"x196.5" | 10 | 1x4 | 1200 | 11.2 | 15 | 15 | 21.4 | 20.9 | 208/60/3
RDS 043 | 48.5"x196.5" | 10 | 1x4 | 1300 | 11.2 | 15 | 15 | 24.8 | 23.3 | 208/60/3
RDS 049 | 48.5"x244.5" | 10 | 1x5 | 1500 | 14 | 15 | 15 | 27.7 | 26.6 | 208/60/3
RDS 054 | 48.5"x244.5" | 10 | 1x5 | 1675 | 14 | 15 | 15 | 31.6 | 29.1 | 208/60/3
RDS 068 | 48.5"x292.5" |  | 1x6 | 1955 | 16.8 | 17.5 | 20 | 39.9 | 36.7 | 208/60/3
RDS 079 | 48.5"x340.5" |  | 1x7 | 2250 | 19.6 | 20.3 | 25 | 46.4 | 42.7 | 208/60/3
RDD 030 | 93.5"x100.5" | 10 | 2x2 | 1002.658 | 11.2 | 15 | 15 | 16 | 16.3 | 208/60/3
RDD 039 | 93.5"x100.5" | 10 | 2x2 | 1106.596 | 11.2 | 15 | 15 | 21.4 | 20.9 | 208/60/3
RDD 043 | 93.5"x100.5" | 10 | 2x2 | 1215.316 | 11.2 | 15 | 15 | 24.6 | 23.1 | 208/60/3
RDD 058 | 93.5"x148.5" | 10 | 2x3 | 1594.894 | 16.8 | 17.5 | 20 | 32.3 | 31.5 | 208/60/3
RDD 064 | 93.5"x148.5" | 10 | 2x3 | 1757.974 | 16.8 | 17.5 | 25 | 36.8 | 34.5 | 208/60/3
RDD 077 | 93.5"x196.5" | 10 | 2x4 | 2043.192 | 22.4 | 23.1 | 25 | 42.8 | 41.8 | 208/60/3
RDD 086 | 93.5"x196.5" | 10 | 2x4 | 2260.632 | 22.4 | 23.1 | 25 | 49.5 | 46.5 | 208/60/3
RDD 098 | 93.5"x244.5" | 10 | 2x5 | 2675.853 | 28 | 28.7 | 30 | 55.3 | 53 | 208/60/3
RDD 108 | 93.5"x244.5" | 10 | 2x5 | 2991.728 | 28 | 28.7 | 30 | 63.3 | 58.2 | 208/60/3
RDD 136 | 93.5"x292.5" | 10 | 2x6 | 3537.03 | 33.6 | 34.3 | 35 | 79.8 | 73.5 | 208/60/3
RDD 158 | 93.5"x340.5" | 10 | 2X7 | 4092.332 | 39.2 | 39.9 | 40 | 92.7 | 85.3 | 208/60/3

## R22 Subcool
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | RACK | SYSTEM | SUCTION | COND TEMP | LIQUID | BTU/HR | TONS
MODEL | SIZE | FPI | FANS | WEIGHT | FLA | MCA | MOPD | R22 | R502 | B | -15 | -15 | +110 | +50 | 111.3 | 9.275 | 1709.939 | 18.171 | 31071.3016
KAC 22 | 48"X98" | 10 | 2 | 465 | 12.8 | 14.4 | 25 | 12.6 | 12.4 | B | -25 | -25 | +110 | +50 | 0 | 0 | 0 | 18.171 | 0 | 31.0713
KAC 25 | 48"X98" | 10 | 2 | 495 | 12.8 | 14.4 | 25 | 12.6 | 12.4
KAC 29 | 48"X98" | 10 | 2 | 520 | 12.8 | 14.4 | 25 | 12.6 | 12.4 | C | -15 | -15 | +110 | +50 | 0 | 0 | 0 | 18.171 | 0
KAC 31 | 48"X98" | 10 | 2 | 550 | 12.8 | 14.4 | 25 | 15.2 | 15 | C | -25 | -25 | +110 | +50 | 0 | 0 | 0 | 18.171 | 0 | 0
KAC 35 | 48"X98" | 10 | 2 | 600 | 12.8 | 14.4 | 25 | 16.9 | 16.6
KAC 42 | 48"X146" | 10 | 3 | 800 | 19.2 | 20.8 | 30 | 18.9 | 18.6
KAC 48 | 48"X146" | 10 | 3 | 900 | 19.2 | 20.8 | 30 | 22.9 | 22.5 | D | -15 | -15 | +110 | +50 | 0 | 0 | 0 | 18.171 | 0
KAC 55 | 48"X146" | 10 | 3 | 1000 | 19.2 | 20.8 | 30 | 25.4 | 25 | D | -25 | -25 | +110 | +50 | 0 | 0 | 0 | 18.171 | 0 | 0
KAC 58 | 48"X194" | 10 | 4 | 1050 | 25.6 | 27.2 | 40 | 25.2 | 24.8
KAC 62 | 48"X194" | 10 | 4 | 1100 | 25.6 | 27.2 | 40 | 30.5 | 29.9
KAC 67 | 48"X194" | 10 | 4 | 1150 | 25.6 | 27.2 | 40 | 33.8 | 33.2
KAC 72 | 48"X194" | 10 | 4 | 1200 | 25.6 | 27.2 | 40 | 33.8 | 33.2
KAC 59 | 96"X98" | 10 | 4 | 1080 | 25.6 | 27.2 | 40 | 25.2 | 24.8
KAC 63 | 96"X98" | 10 | 4 | 1140 | 25.6 | 27.2 | 40 | 30.5 | 29.9
KAC 68 | 96"X98" | 10 | 4 | 1190 | 25.6 | 27.2 | 40 | 33.8 | 33.2
KAC 73 | 96"X98" | 10 | 4 | 1240 | 25.6 | 27.2 | 40 | 33.8 | 33.2
KAC 83 | 96"X146" | 10 | 6 | 1640 | 38.4 | 40 | 50 | 37.8 | 37.1
KAC 95 | 96"X146" | 10 | 6 | 1840 | 38.4 | 40 | 50 | 46.7 | 45.9
KAC 102 | 96"X146" | 10 | 6 | 2050 | 38.4 | 40 | 50 | 50.7 | 49.9
KAC 116 | 96"X194" | 10 | 8 | 2150 | 51.2 | 52.8 | 70 | 50.4 | 49.5
KAC 127 | 96"X194" | 10 | 8 | 2250 | 51.2 | 52.8 | 70 | 60.9 | 59.9
KAC 134 | 96"X194" | 10 | 8 | 2350 | 51.2 | 52.8 | 70 | 67.7 | 66.5
KAC 144 | 96"X194" | 10 | 8 | 2460 | 51.2 | 52.8 | 70 | 67.7 | 66.5
KAC 158 | 96"X242" | 10 | 10 | 2800 | 64 | 65.6 | 80 | 76.1
KAC 168 | 96"X242" | 10 | 10 | 2950 | 64 | 65.6 | 80 | 84.5
KAC 180 | 96"X242" | 10 | 10 | 3075 | 64 | 65.6 | 80 | 84.6
KAC 190 | 96"X290" | 10 | 12 | 3400 | 76.8 | 78.4 | 100 | 91.4
KAC 202 | 96"X290" | 10 | 12 | 3620 | 76.8 | 78.4 | 100 | 101.4
KAC 216 | 96"X290" | 10 | 12 | 3750 | 76.8 | 78.4 | 100 | 101.5
4)CC3-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 32.31
4)CC4-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 37.55
4)CC5-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 41.17
4)CC6-35-108 |  | 10 | 6 |  | 33.6 | 35 | 50 | 43.38
4)CC3-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 40.62
4)CC4-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 47.3
4)CC5-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 52.32
4)CC6-35-128 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 55.11
2)CC4-35-180 |  | 10 | 6 |  | 33.6 | 35 | 50 | 35.32
2)CC4-35-90 |  | 10 | 3 |  | 16.8 | 18.2 | 30 | 17.64
2)CC4-35-120 |  | 10 | 4 |  | 22.4 | 23.8 | 30 | 23.56
2)CC4-35-150 |  | 10 | 5 |  | 28 | 29.4 | 40 | 29.44
2)CC4-35-180 |  | 10 | 6 |  | 33.6 | 35 | 50 | 35.32
4)CC4-35-90 |  | 10 | 6 |  | 33.6 | 35 | 50 | 35.28
4)CC4-35-120 |  | 10 | 8 |  | 44.8 | 46.2 | 60 | 47.12
4)CC4-35-150 |  | 10 | 10 |  | 56 | 57.4 | 70 | 58.88
4)CC4-35-180 |  | 10 | 12 |  | 67.2 | 68.6 | 90 | 70.64
2)CC5-35-150 |  | 10 | 5 |  | 28 | 29.4 | 40 | 32.19
4)CC5-35-150 |  | 10 | 10 |  | 56 | 57.4 | 70 | 64.37
VAC 22 | 48"X98" | 10 | 2 | 465 | 12.8 | 14.4 | 25 | 12.6 | 12.4
VAC 25 | 48"X98" | 10 | 2 | 495 | 12.8 | 14.4 | 25 | 12.6 | 12.4
VAC 29 | 48"X98" | 10 | 2 | 520 | 12.8 | 14.4 | 25 | 12.6 | 12.4
VAC 31 | 48"X98" | 10 | 2 | 550 | 12.8 | 14.4 | 25 | 15.2 | 15
VAC 35 | 48"X98" | 10 | 2 | 600 | 12.8 | 14.4 | 25 | 16.9 | 16.6
VAC 42 | 48"X146" | 10 | 3 | 800 | 19.2 | 20.8 | 30 | 18.9 | 18.6
VAC 48 | 48"X146" | 10 | 3 | 900 | 19.2 | 20.8 | 30 | 22.9 | 22.5
VAC 55 | 48"X146" | 10 | 3 | 1000 | 19.2 | 20.8 | 30 | 25.4 | 25
VAC 58 | 48"X194" | 10 | 4 | 1050 | 25.6 | 27.2 | 40 | 25.2 | 24.8
VAC 62 | 48"X194" | 10 | 4 | 1100 | 25.6 | 27.2 | 40 | 30.5 | 29.9
VAC 67 | 48"X194" | 10 | 4 | 1150 | 25.6 | 27.2 | 40 | 33.8 | 33.2
VAC 72 | 48"X194" | 10 | 4 | 1200 | 25.6 | 27.2 | 40 | 33.8 | 33.2
VAC 59 | 96"X98" | 10 | 4 | 1080 | 25.6 | 27.2 | 40 | 25.2 | 24.8
VAC 63 | 96"X98" | 10 | 4 | 1140 | 25.6 | 27.2 | 40 | 30.5 | 29.9
VAC 68 | 96"X98" | 10 | 4 | 1190 | 25.6 | 27.2 | 40 | 33.8 | 33.2
VAC 73 | 96"X98" | 10 | 4 | 1240 | 25.6 | 27.2 | 40 | 33.8 | 33.2
VAC 83 | 96"X146" | 10 | 6 | 1640 | 38.4 | 40 | 50 | 37.8 | 37.1
VAC 95 | 96"X146" | 10 | 6 | 1840 | 38.4 | 40 | 50 | 46.7 | 45.9
VAC 102 | 96"X146" | 10 | 6 | 2050 | 38.4 | 40 | 50 | 50.7 | 49.9
VAC 116 | 96"X194" | 10 | 8 | 2150 | 51.2 | 52.8 | 70 | 50.4 | 49.5
VAC 127 | 96"X194" | 10 | 8 | 2250 | 51.2 | 52.8 | 70 | 60.9 | 59.9
VAC 134 | 96"X194" | 10 | 8 | 2350 | 51.2 | 52.8 | 70 | 67.7 | 66.5
VAC 144 | 96"X194" | 10 | 8 | 2460 | 51.2 | 52.8 | 70 | 67.7 | 66.5
VAC 158 | 96"X242" | 10 | 10 | 2800 | 64 | 65.6 | 80 | 76.1
VAC 168 | 96"X242" | 10 | 10 | 2950 | 64 | 65.6 | 80 | 84.5
VAC 180 | 96"X242" | 10 | 10 | 3075 | 64 | 65.6 | 80 | 84.6
VAC 190 | 96"X290" | 10 | 12 | 3400 | 76.8 | 78.4 | 100 | 91.4
VAC 202 | 96"X290" | 10 | 12 | 3620 | 76.8 | 78.4 | 100 | 101.4
VAC 216 | 96"X290" | 10 | 12 | 3750 | 76.8 | 78.4 | 100 | 101.5