| Revision Date: 7/18/2024 | 11133/25/1411111 |
| --- | --- |

| Store #: | 2654 |
| --- | --- |

| Store # |  | 2654 | Enter All Quantities in these columns |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| PART ID | QTY | DESCRIPTION | Rack A | Rack B | Rack C | Rack D |
| 10349-1 | 1 | VLV,SOL,REF,NC,7/16PX 5/8 ODF,ME14S250 For Prep/Produce | 1 |  |  |  |
| 95630 | 1 | COIL,SOL,120/208V,SPORLAN,MKC-2 DUAL VOLT | 1 |  |  |  |
| 92398 | 1 | Split cond pumpout kit (exist 2x4 & > & new conds.) 3/8" Purge valve for | 1 |  |  |  |
| 92399 | 1 | B35284 Xducr valve | 1 |  |  |  |
| 10174-1 | 1 | 3/8 SPUN | 1 |  |  |  |
| 88576 | 1 | ORIFICE, 2449-004, .032 | 1 |  |  |  |
| 03381 | 1 | 1/4" Female Flare x 3/8" M Flare Adapter A 05041 | 1 |  |  |  |
| 10389 | 1 | MKC1-208 | 1 |  |  |  |
| 94533 | 1 | E3S130 | 1 |  |  |  |
| 105674 | 2 | Replacement float assembly for flanged oil separators, includes gasket | 1 | 1 |  |  |
| 81624 | 8 | CPC Temp Sensor Lo Temp, Vend # 501-1122, Bullet, 20' | 4 | 4 |  |  |
| 95052 | 1 | LT Case Defrost dump valve kit, OE9S240 |  | 1 |  |  |
| 10394 | 1 | OMKC-2-120V |  | 1 |  |  |
| 104493 | 1 | 0150322H Fuse Holder |  | 1 |  |  |
| 03293 | 1 | 312005 5A,250V,Fast Acting |  | 1 |  |  |
| 105661 | 1 | Fan Klixon,Disc,Close on Rise,60D,3/8" |  | 1 |  |  |

* NOTE: Please refer to drawings on the last pages for correct piping for Reclaim Water Heater, Split Pump-Out and Remote Header Suction Riser.

* NOTE- C02 addendum has been added to RC’s scope of work. NOTE*

- The Refrigeration Contractor will wear a Safety Yellow reflective vest while doing work in the stores. It will need to be a Class II fire resistance vest with your company’s name on the back.

- Refrigeration contractor will have a job trailer on site for storing all job-related materials, case trim, and refrigeration parts until being installed.

  - Trim crew installs all case trim. The exceptions are, interior case trim (will be installed by the RC the night of the cases being relocated), any existing or new kick rails. RC will reinstall anything he removes during relocating a case and any trim that comes with a new case. All 1" bumper on NEW case lines ups. Any line ups with EXISTING cases the 1" bumper will be installed by the painters.

  - It is the refrigeration contractor’s responsibility to ensure that all case parts, trim, and refrigeration parts provided by Food Lion are not lost, damaged or stolen.

  - Any material provided by Food Lion that is lost, damaged or stolen will be replaced by the refrigeration contractor at their expense.

- Case trim needs to be put on during the remodel as lineups of cases are installed.

  - Refrigeration contractor needs to secure any loose trim on existing cases that is not getting replaced.

- All kick plates will be removed by the RC for floor tile work at day of pre-con. There may be some new kick rails that will be replace and that will be listed on the case parts list you receive with the bid package.

  - Kick rails need to remain off until plumbing and other inspections that are required are complete. These kick rails will be placed in the RCs job trailer or trapeze hanger in the back room until time for the RC and/or Vendor to re-install.

  - Old kick plates must be removed. Do not scab new kick plates over old ones.

  - (Case parts will be supplied by case manufacturer)

EXCEPTION: existing Tyler or Hussmann trim by others.

- Refrigeration contractor will be responsible for installing case drains and meeting inspection criteria.

- Case drains shall not be teed together, 2 cases into one hub shall be 90-degree bends into or over hub. Reducing drain line size below case outlet size not allowed.

- All new, relocated, and existing cases shall be sealed, flashed and rodent proofed.

- Back of Deli cases need to be flashed with stainless to the floor and caulked.

- Seal any gaps in the back-to-back frozen food fan plenums.

- Fan plenums need to be added to frozen food cases when installing additional cases to the lineup. These need to be sealed to the top of the cases and end promos to force air to be drawn under cases. Sealing end promos to include existing cases as well.

- Refrigeration contractor will sand and paint the shelf rails in the back of the cases getting interiors PRIOR to the new interiors going in.

- All cases that have new interior skins refrigeration contractor will neatly cut out Model & Serial number and all other NSF, CRMA, UL, etc. decals and screw them to the top of the case or under the bottom of a single deck type case.

- Trim needs to be completed by the 100% completion date on the remodel schedule.

- Contact Case Manufacture with all missing items ASAP.

- Remove produce hanging scales from existing cases that are being removed or relocated. These are to be reinstalled on each side of the wet case.

- Remove all old-style air flow shelving from the produce salad cases.

- Replace all existing shelving in relocated cases to their original positions.

- Refrigeration contractor will install new suction, liquid, and oil filters in all racks before cutting into any systems or beginning any refrigeration work.

- Suction, liquid, and oil filters will be changed out 30, 60, 90 days after the refrigeration modifications. Per Spec.

- The suction filters are to be removed at the 90-day change and springs left wire tied to rack.

- At the 90-day filter change replace the float in the oil separator. This will be supplied by the rack manufacture.

- Add high water capacity liquid line filters before cutting into system. These will be used until last refrigeration modification. Then removed and standard filters need to be installed.

- All POE oil systems to have RCW liquid dryers on last change.

- Run new refrigerant lines overhead to all new and relocated cases and walk in evaporators. Reuse of existing lines permitted but must comply with summary and meet Food Lion approval. This will be determined prior to bid.

- When straightening the FF/IC line ups all new lines or insulation repairs/replacement to existing line sets on top of the cases will need to be in your bid.

- Install drip pans under all lines above all suspended ceilings Per Spec.

- Pans are to be hung at the same time the refrigeration lines are installed.

- Any drip pans that are presently installed, will need to be checked for improper installation and leaks and either repaired or replaced.

- If open ceiling stores does not have drip pans you shall install them. This will be for all lines in sales area and above backroom ceiling and the deli and produce areas.

- Insuguard™ pipe cradles shall be used on all refrigeration piping. Please separate Suction and Liquid line in separate cradles where space allows and for new hangers. This will include separate cradles for piping ran on top of cases as space allows. The piping under deli cases will remain as single cradle for both suction and liquid combined. The only exception will be where they will not physically fit, or the piping is Hydra-Zorb™ clamped in the machine room. If cradles will not fit, lines are to be supported with ¾” insulation over ¾” strut or PVC every four foot on case tops, and six feet between overhead pipe hangers.

- Any refrigeration circuit's line sets that will be reused or is existing that needs the insulation replaced per the scope of work will use Armaflex Lapse Seal and factory-made fitting covers for the 90-degree ells. All new line sets will use the traditional slide on type as before.

- Coordinate location of new or relocated risers and line sets with Energy Team member.

- Any cases that will be installed new or relocated, that will use under floor conduit and pits, must have new refrigerant lines.

- GC needs to have fiberglass boxes for all pits at job site!!!  If for some reason you can't dig deep enough to install a full box the box can be cut shorter and pour concrete in the bottom to rodent proof. Good workmanship is a must when installing these pits.

- Any pre-existing pits that will be used must either be sealed concrete pits or new fiberglass pull boxes. No dirt pits will be acceptable.

- Call the Energy Team member over the job immediately if this problem exists.

- If you set cases on any dirt pits, you will be asked to move the cases to correct the problem at your expense!!!

- The GC will be responsible for sealing the new fiberglass pits and fill and concrete any existing pits that will not be used.

- The Refrigeration Contractor will be responsible to seal the PVC inside with foam where your lines come into the pit.

- The use of any under floor conduits, pits and line-sets will be determined by the Energy Team only. Do not plan to use these without his permission and direction.

- If any drains or pits aren’t done correctly or they are in the wrong location the Refrigeration Contractor will not set the case and will contact us immediately. If the RC does set a case over a pit or drain that isn’t correct without calling us, he will move it at his expense so it can be corrected. Pits are for refrigeration, not electrical or plumbing!

- Refrigeration contractor will need a day tech after each night with a case move. He shall be there by 7:00 AM the next morning. The tech will need to ensure all work that night is completed to Food Lions spec, line sets insulated correctly, all supports in place on top of case, penetrations sealed, etc. He will need to complete Energy Team’s field reports, verify shielded cable is terminated at the rack and the case, EPRs are adjusted, superheat set if possible, controller programed if a new circuit, defrost terminations working on all cases from previous night’s work.  The tech will trouble shoot and repair any problems that may occur the next morning. Once he has all issues 100%, he may leave. If he leaves and the Energy team member finds issues he will be called back out. If there is a night with no case move no tech will need to be there the next morning.

- The Refrigeration contractor will have a minimum of six people the week of the frozen food case moves. This will be if replacing all frozen food and ice cream cases in one week.

- Field top stub all relocated cases. Example: FF end caps. (Unless instructed by Energy Team to do differently)

- If cases show up that are not top stubbed, that was supposed to, top stub in the field and notify Energy Team member over job.

- Do not run lines behind cases. All top stubs need to be connected to main line on top of cases using inverted traps and teed into the top of the main line using reducing tees.

- All inverted traps on top of cases are to be painted the same color as the walls, when exposed above valance. Keep traps as low as possible.

- Lines are to be supported on the top of cases with saddles. Liquid and suction in separate saddles where space allows. If there is not ample space on top of case and lines will get in the way of the valiance install, use ¾” insulation over ¾” unistrut or ¾” insulation over ¾” PVC every four foot and wire tie to the support.

- All exiting cases that are NOT RELOCATING that have piping behind the case and has overhead line sets MUST be top stubbed. MAKE SURE THIS GETS IN YOUR BIDS ON ALL SPENDS.

- Medium temp and low temp racks with split suction headers at two different suction operating temperatures are to be tied together at the compressor suction headers and the suction crossover is to be opened.

  - You will need to check with the rack manufacturer for proper piping size as to not have a pressure drop between headers.

  - If you do not have this information, contact the rack manufacture or Energy team member.

- All split discharge headers are to be tied together and ran through a single oil separator.

- The oil separator will need to be sized for the rack and replaced if not large enough.

- You will need to add a check valve above any oil separator that does not have one.

- Remove all hot gas defrost piping and associated valves and wiring from all medium temp racks.

- Cap off all line stubs.

- No pinched lines.

- NOTE: Pull all unnecessary and abandoned refrigeration circuit and hot gas wiring out of racks and back to electrical trough.

- Install EPR and other associated components for additional circuits. Replace all suction stops with SORIT EPR valves if reflected by rack summaries and/or parts list. Except Parker suction stops, Food Lion will provide kit to convert these to EPR’s.

- These to be supplied by rack manufacturer.

- New EPR pilot lines need to be ultra-tubes.

i.    Remove all existing black and braided super-hoses and replace with Ultra-Tubes

- On a rack with no EPR’s, you must make a hot gas pilot header. This header will need a ball valve to isolate it from the main system.

    - Also, it will need ¼ inch Mueller A14838 sweat ball valves for each EPR hot gas pilot.

- If the racks have any existing Product Engineering or Alco valves, (split condenser, heat reclaim, discharge regulator, EPR, etc.), they are to be changed to Sporlan valves.

- If a rack has a new split condenser added, or if it has a split condenser that is piped as single, the rack is to be piped for split condenser operation.

- Install a ¼ check valve on the pilot line on any existing medium temp rack with split if needed.

- If the existing racks have a split condenser has more than 6 fans you are to install a secondary pump-out kit on the (half season or split side) of the liquid drop leg above the check valve and pipe it to a Mueller A14838 sweat valve and to the suction header. This kit will be provided by RACK MFG.  See schematic on later page.

- Insulate both supply and return line to water reclaim.

- Wire racks that have both water and heat reclaim so that both can work at the same time.

- Pipe discharge through the water 3-way valve first then through the air reclaim valve.

- Water reclaim shall have the full capacity of the rack.

- A four-wire shielded cable will be ran from the refrigeration rack to both reclaim water heaters and sensors will be installed per Food Lion drawing attached. Then controls will be set up to operate water reclaim using these temp sensors as maximum control.

- Both water reclaim tanks are to be piped from the low temp rack

- Wire rack for 2nd stage heat reclaim if not currently set up.

- Remove all surge valves and associated wiring. Install a ball valve for isolation in its place.

- If subcooler does not have an ORIT valve, install one.

- Make any necessary repairs to the subcooler to make it operate at 45 deg liquid.

  - Racks will need ample refrigerant with no flash gas for the subcooler to work properly.

- Install dual pressure controls on compressors that currently do not have them or per parts list.

  - Replace all hoses with Ultra-Tubes™.

- Replace all caps that are currently missing.

- Remove all bad inverters, and their contactors, wiring, toggle switches and boards completely from the racks and rewire compressor control circuit for standard compressor control.

- Clean up all unnecessary wiring and make sure to use PVC Wiring Duct where needed.

- All new wiring in racks for new or existing circuits and control wiring needs to be #18 stranded copper wires.

  - Parts added to Rack will need to be ran in Poly-Tuff type flex conduit and not metal flex if new electrical is required.

- Replace all mechanical door switches with new magnetic switches provided by the case manufacture. Electrician to pull a 4 wire 22 ga. shielded cable if needed. Refrigeration contractor to terminate at both ends. The 4 wire 22 ga. shielded cable is for the door switch.

- The Refrigeration contractor is now responsible for final sensor cable termination, for case temp sensors and defrost termination at the rack/header control cabinet and at the cases/walk-in boxes for all new, existing, and relocated cases/walk-in boxes.

- The refrigeration contractor is responsible for adding and mounting any necessary temp sensors in existing/ relocated/new cases/walk-in boxes where needed.

  - NOTE: New cases should come with sensors.

  - It is still the EC’s responsibility to install wiring and shielded cable for the cases/walk-in boxes and door switches for the correct refrigeration circuit and route to the Rack/Header control cabinet.

  - The EC is also responsible for tagging wires in the Rack/ Header control cabinet and the cases/ walk-in boxes with the proper circuit designation.

  - The EC will still be responsible if the circuit is open, shorted, or crossed.

  - NOTE: These must be working 100% the night/day of cases/ cooler installation.

- The Refrigeration Contractor is to replace any gang clocks that may be in any rack that will remain after the remodel.

- Sensors to be installed to all existing circuits and any circuits not having sensors.

  - Extra boards may be needed to accommodate additional sensors.

  - The Energy Team member will provide any needed boards.

- Suction temp sensors are to be installed to all racks at the outlet of each suction filter.

- When installing new rack controllers or a new rack, controller communications are to be operational ASAP for alarming feature and communications.

- Add input and output boards to accommodate circuit additions.

  - Energy Team Member will provide boards.

  - Refer to refrigeration summary sheets for specific location of all circuit placements on racks.

- Make sure controller is programmed to Food Lion set point guide specifications.

- Repair or replace all bad insulation on racks and tops of cases.

- Replace loose or broken clamps and hangers on the existing racks.

- Repair or replace any separation in insulation that can be easily repaired by gluing joints and black insulation tape in motor room, Walk-ins, stock room and above ceiling while piping new circuits.

- Remove all unused and unnecessary piping, pans, and hangers in motor room and throughout store.

- Use appropriate caps to seal off all unused circuits. (No pinching the lines)

- Install the New ROF oil filter kit provided by the Rack Manufacturers on all existing racks.

  - Use only mounting brackets provided in kit to mount the new oil filter.

  - Install 3/8’s ¼ turn shut off valve with pressure tap on the down stream side off oil filters, so they may be readily isolated.

  - Install pressure tap on the oil filter side for drainage. (Supplied by the rack manufacturer)

  - Strap oil filters to rack on vertical steel upright in the upright position, install horizontal steel uni-strut to mount it as needed.

  - Oil filter to be in high pressure line prior to reservoir, if not relocate.

- Install a liquid line solenoid and coil for the produce prep/garden cooler circuit at the rack down stream of the liquid line ball valve if there is not one currently on the rack.

  - Wire the liquid line solenoid coil in parallel with the EPR solenoid coil.

  - Cut out produce prep solenoid above produce prep room and cap wiring if applicable.

  - For racks with RMC, RMCC controllers the mechanical contractor will run a 2-wire shielded cable from EMS panel to the rack with the produce prep circuit. The RC will need to daisy chain the wiring for the produce prep temp sensor on the 16AI board in the EMS panel to a spare 16AI board in the rack. Note: the dip switch must be in the down position in the EMS panel and the up position on the 16AI board in the rack to read correctly.

  - For racks with RMC controllers, it will be necessary to set up a spare output on an 8RO board for temperature control through the sensor control field. You will need to series the control wire feeding the produce prep EPR and Liquid line solenoid through this 8RO BDPT. Note: this board point will be wired NC and the dip switch up.

  - For E2 controllers you will not need to run the shielded cable, this can be done through global network.

  - Program controllers for this application.

- All new condensers will need a ¼ angle Henry valve installed on the inverted trap.

  - Make sure all inverted traps in the supply line to the condenser are located far enough away from the electrical door on the condenser so it can open at a 90 deg angle.

- If refrigerant conversion required refer to Conversion scope provided by Maintenance Manager.

- Updated rack summaries are to be laminated and attached to racks.

- If a new rack with (R407A) is installed and the existing rack is (R22) all existing cases and     walk-ins must have caps and schraders replaced. Also, all packing’s on TXV’s and Henry valves must be tightened.

- Each motor room is to have a current fixture plan labeled with new circuits and installed behind Plexiglas on door.

  - Show all temp sensor locations in all cases using a * or S.

- All cases, walk-in coolers and prep rooms are to be labeled.

  - Labels will be supplied by rack manufacturer.

- All case manufacturers literature for the cases and racks are to be left in the motor room for the Maintenance Tech.

- Wash motor room after completion of work.

- Clean all honeycomb in existing medium temp cases and all evaporator coils in coolers and prep rooms after construction is complete.

- Refrigerants will be supplied by Refrigeration Contractor and shall follow the refrigeration summary/Identification that is marked on rack to identify the correct refrigerant type. Use only the refrigerant in equipment for which that equipment was designed by the manufacturer.  Use only one type of refrigerant in a system.  The refrigerant shall be delivered to the job in original Virgin containers.

- On day of pre-construction meeting refrigeration contractor and a Retail Business services appointed maintenance supervisor or field energy specialist will verify refrigerant percentages of existing systems prior to starting work and sign off on the refrigerant log posted on the refrigeration racks under the following rack conditions.

  - Rack running normal for 20 minutes, without any circuits in defrost, no water reclaim, no air reclaim and no split condenser.

  - After 20 minutes of normal run time and levels are 10% or 1 ball floating or above, then document the levels and sign off.

  - After 20 minutes of normal run time if there is not 10% in receiver or 1 ball floating, Maintenance will bring levels up to 10% or 1 ball floating either by in house technician or a work order will be opened for the RC to bring levels up to 10% in receiver or 1 ball floating and then sign off.

- Refrigeration contractor will be required to leave in motor room three deposit valued cylinders of refrigerant secured to wall and maintained throughout remodel for all conditions that may arise throughout the remodel this will include three deposit valued cylinders for each type of refrigerant in racks.

- At the completion of the RCC all refrigerant levels will be confirmed by a Retail Business services appointed maintenance supervisor or field energy specialist to the levels and conditions that were signed off on at pre-construction meeting.

- If no refrigerant was used at the completion of the RCC, from the supplied refrigerant tanks by the refrigeration contractor, they can remove at that time.

- All Food Lion specs and warranties will be adhered to in accordance with remodel specifications and Energy Team’s instructions.

- Contractors will be responsible for ALL refrigeration calls starting on the Precon date, until the end of the warranty period; this includes new, relocated, and existing cases and machine room equipment.

  - The Refrigeration Contractor will be required to supply a backup contractor after hours and on weekends. If the call is on existing equipment and not the fault of the Refrigeration contractor, he will be paid for that call after the approval of the Maintenance Supervisor.

  - The Refrigeration Contractor will notify the Maintenance Supervisor as to any problems or loss product that might occur during this time. The Maintenance Supervisor will evaluate for responsibility of payment.

  - The Food Lion Maintenance dispatchers will NOT reassign tickets based on comments from the contractor. If the problem is an existing one, the ONLY way the work order can be reassigned is for the contractor to contact the Maintenance Supervisor or Technician, who will advise the dispatchers if the work order is to be reassigned to someone other than the renewal contractor.

- Make all changes as highlighted on refrigeration summary for case changes and verify with fixture plan.

  - Contact the Energy Team member assigned to job if there are any discrepancies.

  - No deviations are to be made from the refrigeration summary without authorization from the Energy Team member.

  - All changes and discrepancies are to be checked through the case manufacture for proper sizing and load.

- New frozen food and I/C glass door cases with t-stat to shut off lights and anti-sweats during defrost will set at 0º for I/C cases and +10º for frozen food cases. Then silicone dial. ALL new Kysor FF and IC need bottom frame A/S secondary connected in raceway.

- RC is responsible for setting superheat and EPR’s on existing Medium Temp cases that have retrofit doors installed. This to be done morning after the doors are installed.  Also install T stat and solenoid if needed for any system with doors and open cases on same circuit. It shall be installed on door section cases only and rack EPR to control open case temperature.

- The Refrigeration Contractor will install manufacturer’s provided motion sensors on the frozen     food and ice cream glass door cases with LED lighting. These sensors will be mounted in the center of each case. ONLY install on cases opposing other refrigerated cases! No end caps will get motion sensors. If you have questions on where to mount these sensors, please contact the Food Lion Energy Team member. The setting on the sensor will be dim to 20%, delay after    detection is 1 minute.

- RC to install check valve above oil separator if the existing racks do not have them.

Parts supplied by rack manufacturer.

- The RC needs to check the M1.01 or the M6.01 to see if a new heat reclaim coil is being added to any new or existing Air Handler in the store. If a coil is added the RC will pipe it the same as the condenser line set.

- Need to pipe the receiver relief valve for all racks through the roof. Follow the condenser lines through the pitch pocket. Pipe size should be 7/8 copper up to (2) racks, 1 1/8 for (3) racks and   1 3/8 for (4) racks. Add a u-bend to prevent rain from entering; Relief location must be piped 20’ away from ventilation openings and 15 ft off the ground. or meet local and state codes.

- When changing a 4D or 6D to a 2D or 3D add a current sensing relay to the 240 wire to the oil control.

84.

## Evacuation Requirements

### Appliances with More than Five Pounds of Refrigerant

Technicians must evacuate air-conditioning and refrigeration equipment to established vacuum levels when opening the equipment for maintenance, service, repair, or disposal. The required level of evacuation can be found in the following table.

# Required Level of Evacuation of Appliances

This table lists levels of evacuation for various types of refrigeration and air conditioning equipment manufactured either before or after November 15, 1993.

| Type of Appliance | Inches of Hg vacuum (relative to standard atmospheric pressure of 29.9 inches Hg) |  |
| --- | --- | --- |
|  | Using pre-1993 equipment | Using post-1993 equipment |
| Very high-pressure appliance | 0 | 0 |
| High-pressure appliance, or isolated component of such appliance, with a full charge of less than 200 pounds of refrigerant | 0 | 0 |
| High-pressure appliance, or isolated component of such appliance, with a full charge of 200 pounds or more of refrigerant | 4 | 10 |
| Medium-pressure appliance, or isolated component of such appliance, with a full charge of less than 200 pounds of refrigerant | 4 | 10 |
| Medium-pressure appliance, or isolated component of such appliance, with a full charge of 200 pounds or more of refrigerant | 4 | 15 |
| Low-pressure appliance | 25 mm Hg absolute | 25 mm Hg absolute |

## Exceptions to the Evacuation Requirements

EPA allows limited exceptions to the evacuation requirements for 1) repairs to leaking refrigeration and air-conditioning equipment.

### Repairs to Leaking Equipment

If technicians cannot evacuate to the specified levels because of refrigerant leaks, or because it would substantially contaminate the refrigerant being recovered, they must:

- Isolate leaking components from non-leaking components wherever possible;

- Evacuate non-leaking components to the specified levels; and

- Evacuate leaking components to the lowest level that can be attained without substantially contaminating the refrigerant. This level cannot exceed 0 pounds per square inch (psig).

* NOTE C02 ADDENDUM NOTES*

- RC to provide and maintain a full rack refrigerant charge onsite and maintained until install is completed. At that time refrigerant can be transferred to Foodlion inventory.

- RC to provide 2 gallons of unopened refrigerant oil onsite as recommended by the compressor manufacturer.  The oil will be specifically formulated for use in a trans critical applications.

- RC to have on hand all the necessary tools, gauges charging manifolds etc. Rated for R744.

- RC to have on hand lap-top and program app Wiz-Mate and knowledge of how to program X679 case controllers per manufacture/Foodlion specifications.

- RC to provide and install 1-inch wall insulation to suction and liquid lines on both medium and low temp circuits.

- RC will provide correct size cradles for suction and liquid lines, one cradle for liquid line and one cradle for suction line.

- RC to terminate both ends of the 485 communications loops and ensure the cables circuit tags are clearly and accurately remarked when terminating ends.

- RC to install C02 high visible refrigerant directional refrigerant flow tape it is recommended that labeling comply with ANSI/ASME Standard. A13.1-81, “Scheme for the Identification of Piping Systems.” No more than 20 feet apart.

- RC to take possession and secure the program flash keys provided by the case manufacturer inside of the rack controller.

- All system components will be selected to operate with R744 within the limits of the pressure extremes which the system operates.

- All store copper piping from the rack to/from the cases and walk-ins shall be ACR type K.

- All discharge/return line piping to/from the rack system and the gas cooler and any interconnecting piping to/from air handler directly exposed to CO2 refrigerant on the high side shall be high pressure copper tubing with associated fittings (Mueller XHP or Wieland K65) is acceptable in lieu of certified TIG welded steel piping.

- All sweat-type copper fittings shall be suitable for R744 refrigerant and the associated pressures which will be dependent on the rack manufacturer.  All elbow and return bends shall be 90-degree long radius.  Traps in risers shall be factory fabricated traps such as Mueller Brass Co. or NDL “P” traps, as per manufacturer recommendations.

- All shut-off hand valves shall be the same port size as the lines in which they are installed.  They shall be nonferrous ball valves with seal cap or angle valves. All ball valves will be of internal pressure relief type.

- Pulling Tees is not acceptable “on site” as thinning of the pipe material cannot be controlled.

- The system gas cooler return shall have a dedicated temperature sensor securely mounted, not affected by ambient air and located at the outlet of the gas cooler within 6-inches with 1 ½ inch white insulation and PVC wrapped.

Suction Line Double Riser Detail

Water Heat Reclaim Detail

.

Pump-out for Split Condenser Detail